## Requirements
ID | Domain | Requirement | Source | Kit_status | Product_status | Verification_ref
REQ-REG-001 | Regulatory | CEI 0-16 Annex O/T/M compliant Central Plant Controller | cei-0-16-allegato-o/t | N/A | Required | REQ-PF2-001
REQ-NET-001 | Network | Eth_A logical channel to DSO per EN 61850 (Annex O O.13.1.2) | cei-0-16-allegato-o | Partial 2x GbE | 4-port isolation | L2 MMS client
REQ-NET-002 | Network | Eth_B to Operatore Abilitato — separate from Eth_A | cei-0-16-allegato-t | Partial | Required PHY/VLAN | L2 60870/61850
REQ-NET-003 | Network | Two outside plant network interfaces (O.13.1.1) | cei-0-16-allegato-o | None on kit | Plant x2 on carrier | L2 Modbus TCP
REQ-SER-001 | Serial | 2x opto-isolated RS485 Modbus RTU to energy analyzer | ccli-vendor-selection C2 | 1x RS485 DB9 non-opto | Required carrier | L2/L3 Modbus poll
REQ-IO-001 | Digital I/O | DI 10-120 Vdc x5 external field supply | ccli-vendor-selection C4 | None GPIO only | Carrier opto | L2 DI box
REQ-IO-002 | Digital I/O | DO dry contact x3 for PF2 curtailment | ccli-validation-strategy | SW stub | Carrier relay | L2 DO lamps
REQ-PWR-001 | Power | 12-24 Vdc wide-range isolated product input | ccli-prototype-bom C10 | 7-24V kit bench | Carrier PSU | Bench PSU test
REQ-SEC-001 | Security | Secure boot HAB + signed firmware images | ccli-github-layer-pins | Partial BSP | Required product | Lab secure boot
REQ-SEC-002 | Security | Key storage in secure element / TPM path | ccli-prototype-bom C6 | Verify SoM SKU | Required | Key hierarchy review
REQ-TIME-001 | Time | GNSS timestamp for measurements and events | ccli-vendor-selection C5 | None on kit | Carrier GNSS | L3 PPS capture
REQ-LTE-001 | Cellular | LTE backup / remote monitoring (optional rev A) | ccli-prototype-bom | Optional | Carrier modem | Deferred
REQ-PF2-001 | PF2 | Curtailment command path with safe-state on comms loss | ccli-validation-strategy | SW mock L1 | DO + logic | L2 failure matrix

## Verification_Matrix
Requirement_ID | Description | Test_method | Level | Pass_criteria | Bench_ref | Evidence_path | Status
REQ-NET-001 | Eth_A MMS server | L2: libiec61850 client on isolated NIC | L2 | Read/write logical nodes on Eth_A only | Wave A switch | — | Planned
REQ-NET-002 | Eth_B operator channel | 60870/61850 client on second GbE | L2 | No crosstalk from Eth_A under VLAN test | Wave A | — | Planned
REQ-SER-001 | Modbus RTU poll analyzer | USB-RS485 + pymodbus / real analyzer | L2/L3 | Register map matches DS | Wave A/C | — | Planned
REQ-IO-001 | DI 10-120V sense | 24V DI test box injection | L2 | All channels debounced; no false PF2 | Wave B | — | Planned
REQ-IO-002 | DO curtailment relay | Simulated DSO command toggles DO | L2 | Lamp/relay within timing budget | Wave B | — | Planned
REQ-PF2-001 | Comms loss safe state | Failure matrix: meter/Eth/GNSS stale | L2 | Defined safe state; no unsafe curtailment | Validation strategy §9 | — | Planned
REQ-TIME-001 | GNSS timestamp | PPS/NMEA capture on events | L3 | Sub-second event ordering | Wave C + carrier | — | Deferred
REQ-SEC-001 | Secure boot chain | Signed vs unsigned image boot | Lab | Unsigned rejected; rollback policy | Toradex signed-boot repo | — | Planned
REQ-PWR-001 | Input 12-24V operation | Bench PSU sweep | L2 | SoM boots across range; no rail collapse | Wave A PSU | — | Planned