## Interface_Matrix
Interface | Source | Destination | Protocol | Physical | Isolation | Block | Kit_99991105 | Carrier | RAG_source
Eth_A | CCI SoM+PHY | DSO | IEC 61850 MMS / GOOSE | RJ45 GbE | Separate PHY/VLAN from Eth_B | C1 | GbE port 1 — SW demo | Dedicated PHY + magjack | cei-0-16-allegato-o
Eth_B | CCI SoM+PHY | Operatore Abilitato | IEC 61850 / IEC 60870-5-104 | RJ45 GbE | Separate from Eth_A | C1 | GbE port 2 — SW demo | Dedicated PHY + magjack | cei-0-16-allegato-t
Plant-1 | CCI | Plant LAN / inverters | Modbus TCP / raw Ethernet | RJ45 | Logically separated from DSO path | C1 | Not on kit | Switch port or PHY3 | ccli-prototype-bom
Plant-2 | CCI | Plant HMI / spare | Modbus TCP / spare | RJ45 | Same policy as Plant-1 | C1 | Not on kit | PHY4 / switch | ccli-prototype-bom
RS485-A | CCI carrier | Energy analyzer | Modbus RTU | RJ45 8/8 plant serial | Opto-isolated | C2 | Not CEI-compliant | U-485 transceiver x1 | ccli-vendor-selection
RS485-B | CCI carrier | Spare / IEC 60870-101 | Modbus RTU / 101 optional | RJ45 8/8 | Opto-isolated | C2 | Kit RS485 DB9 lab only | U-485 transceiver x2 | ccli-prototype-bom
DI-1..5 | Field 10-120 Vdc | CCI GPIO via opto | Digital input | Terminal block | Opto + external field supply | C4 | None | U-DI conditioner | ccli-vendor-selection
DO-1..3 | CCI relay driver | Curtailment contactors | Dry contact PF2 | Terminal block | Relay isolation | C4 | SW stub only | K-DO relay | ccli-validation-strategy
GNSS | Antenna SMA | SoM UART/USB | NMEA + PPS | SMA coax | ESD protection | C5 | None | U-GNSS + ANT-G | ccli-prototype-bom
LTE | Modem | Mobile network | PPP/QMI | SMA + SIM | Logical separation from Eth_A | C7 | Optional | U-LTE rev A | ccli-prototype-bom
USB | Service laptop | SoM USB-C/A | Commissioning console | USB | Out of certified control path | C8 | HAVE kit USB | Product service port | ccli-toradex-verdin-devboard
CAN | — | — | Not in CEI CCI minimum | DB9 on kit | N/A product | — | 2x CAN on kit | Not required | ccli-toradex-verdin-devboard