AiLux CCI — Controllore Centrale di Impianto

Cybersecurity, IEC 61850 Data Model, ACSI Services and Communication Timing Requirements

Extracted and consolidated from CEI 0-16:2023-05 V2, Annex T ("Information exchange based on IEC 61850")

Source document: Estratto CEI 0-16 — Allegato T (English translation, CT 316 / CT 57), publication date 2024-12

Status: COMPLETE for Annex T. This document is the companion to "CCI – Mandatory Measurements & Timing (from CEI 0-16 Annex O)" and resolves the items listed there under "13. Open Items — Pending Annex T": IEC 61850 logical-node/data-model mapping, GOOSE/MMS timing performance classes, and the full cybersecurity architecture (PKI, TLS, RBAC, logging). Read together, the two documents form the complete mandatory-requirements baseline for the CCI firmware.

# 1. Purpose and Scope of This Document

This document consolidates every mandatory numerical and structural requirement stated in Annex T of CEI 0-16:2023-05 V2 ("Information exchange based on IEC 61850") that the CCI AiLux firmware must respect: communication timing and performance classes, measurement periodicity, IEC 61850 data-model structure (Logical Devices/Nodes/Data Objects), ACSI services, role-based access control, and the full cybersecurity profile (PKI, TLS, certificate management, logging, time sync, network segregation).

Annex T applies specifically to the CCI–DSO (and CCI–Aggregator) IEC 61850 interface; it does not define communication to the elements inside the plant. Unless noted otherwise, every value below is a hard normative requirement ("shall"), not a design suggestion.

The Annex T data model is split into three independent sections, each separately optional/mandatory:

- Observability — mandatory (unless a specific Data Object is marked Optional in its own table).

- Control — entirely Optional (implemented only if the CCI supports remote control by the DSO).

- Participation in the Dispatching Services Market (Aggregator interface) — entirely Discretionary.

# 2. IEC 61850 Communication Timing (T.3.2.1)

The IEC 61850 server implemented by the CCI is a single logical access point (one IP address). All info below governs the client/server (MMS) exchange between CCI and DSO/Aggregator.

| Data / Function | Sending mode | Performance class (IEC 61850-5) | Presence |
| --- | --- | --- | --- |
| Plant characteristics (static + dynamic config) | On request | Type 3 – low speed messages | Observability, Mandatory |
| Plant operating status | On request + on change | Type 3 – low speed messages | Observability, Mandatory |
| Plant measurements | Periodic, every 4 s | Type 3 – low speed messages | Observability, Mandatory |
| Operating parameter values (control setpoints) | On request + on change | Type 3 – low speed messages | Control, Optional |

- Performance Class Type 3 ≈ P5 ("low speed messages"); expected end-to-end transit time ≈ 500 ms inside the substation (IEC 61850-5, §11.2.2/11.2.3). Outside the substation these exchanges are not catalogued by the standard.

- Power set-point (P/Q) latency is explicitly required as Performance Class Type 3.

- The CCI is not required to publish GOOSE, but shall be able to subscribe GOOSE messages relating to control functions; any such high-speed exchange is required as Performance Class Type 1.

- Mapping: IEC 61850-8-1 over MMS (two-party Client/Server application association), compatible with "Type 2/Type 3" typologies of §5.1 IEC 61850-8-1.

Source (Annex T): T.3.2.1 "Communication modes"; T.3.3.3 "Communication Protocol Mapping".

# 3. Measurement Data Model & Periodicity (T.3.1.3 / T.3.3.1.1.7)

Sampling/transmission period: every 4 s for all measurements below (MMXU logical node, DA "mag").

| Measurement point | Quantity | Unit | IEC 61850 mapping | Presence |
| --- | --- | --- | --- | --- |
| Point of Delivery (PdC) | Active power (signed) | kW | MMXU1 (prefix PdC) . TotW | Mandatory |
| Point of Delivery (PdC) | Reactive power (signed) | kVAr | MMXU1 (prefix PdC) . TotVAr | Mandatory |
| Point of Delivery (PdC) | Phase-to-phase voltages | kV | MMXU1 (prefix PdC) . PPV | Mandatory |
| Point of Delivery (PdC) | Phase currents | A | MMXU1 (prefix PdC) . A | Optional |
| Generation aggregate (PV/Wind/Thermal/Hydro) | Total active power per source | kW | MMXU2 (prefix GenPV/GenWi/GenTer/GenIdr) . TotW | Mandatory |
| Storage aggregate | Active power | kW | MMXU2 (prefix St) . TotW | Mandatory |
| Single Generating Group (SGG), N = 1..99 | Active power | kW | MMXU2 (prefix SGG) . TotW | Mandatory |

Source (Annex T): T.3.1.3 "Information on measurements of electrical quantities"; T.3.3.1.1.7 "Plant measurements".

# 4. Characteristic Power Vector (Table 80) & Nameplate Data Objects

Used both for static nameplate data at the PdC and as the p.u. reference base (Smax) for every control setpoint below.

| Information | Unit | IEC 61850 mapping (DPCC, prefix) |
| --- | --- | --- |
| Maximum active power input (generation) | kW | DPCC1 (PdC_Wi) . WRtg |
| Maximum active power in absorption | kW | DPCC1 (PdC_Wa) . WRtg |
| Maximum inductive reactive power | kVAr | DPCC2 (PdC_Qi) . VArRtg |
| Maximum capacitive reactive power | kVAr | DPCC2 (PdC_Qc) . VArRtg |
| Maximum apparent system power (Smax) | kVA | DPCC3 (PdC_VA) . VARtg |

Source (Annex T): T.3.1 Table 80; T.3.3.1.1.3 "Operating Characteristics at the Connection Point".

# 5. Control-Function Parameters, Ranges and Defaults (T.3.1.4)

All Control, Optional unless marked Discretionary (MSD participation). Every percentage is referred to Smax unless stated otherwise.

## 5.1 Active Power Limitation (Table 85 — LN DWMX, prefix Wlim)

| Parameter | Unit | Range | Default |
| --- | --- | --- | --- |
| Operating status | – | 1 = Operating / 5 = Not-Operating | 5 |
| Active power limit in generation mode | % | 0..100 (ref. Smax) | 0 |
| Activation command | – | 5 = Inactive / 1 = Active | 5 |
| Setpoint function status (from DSO) | – | 0 = Not available / 1 = Autonomous / 2 = Automatic (Priority) | 1 |
| Limit function status, P 110% | – | 0 = Not available / 1 = Autonomous | 2 |

## 5.2 Modulation of Active Power (Table 86 — LN DAGC, prefix WSd)

| Parameter | Unit | Range | Default |
| --- | --- | --- | --- |
| Operating status | – | 1 = Operating / 5 = Not-Operating | 5 |
| Feed-in / feed-out setpoint | % | 0..100 (+feed-in / -feed-out, ref. Smax) | 100 / 0 |
| Activation command | – | 5 = Inactive / 1 = Active | 5 |
| Function status | – | 0 = Not available / 2 = Automatic (Priority) | 2 |

## 5.3 Active Power Set-Point — MSD participation (Table 87 — LN DAGC, prefix WSa) — Discretionary

| Parameter | Unit | Range | Default |
| --- | --- | --- | --- |
| Operating status | – | 1 = Operating / 5 = Not-Operating | 5 |
| Feed-in / feed-out setpoint | % | 0..100 (+feed-in / -feed-out, ref. Smax) | 100 / 0 |
| Activation command | – | 5 = Inactive / 1 = Active | 5 |
| Function status | – | 0 = Not available / 2 = Automatic (Priority) | 2 |

## 5.4 Voltage Control with Reactive Power (Table 88 — LN DVAR, prefix VArSd)

| Parameter | Unit | Range | Default |
| --- | --- | --- | --- |
| Operating status | – | 1 = Operating / 5 = Not-Operating | 5 |
| Feed-in / feed-out reactive power | % | 0..100 (+capacitive / -inductive, ref. Smax) | 0 / 0 |
| Activation command | – | 5 = Inactive / 1 = Active | 5 |
| Function status | – | 0 = Not available / 2 = Automatic (Priority) | 2 |

## 5.5 Reactive Power Set-Point — MSD participation (Table 89 — LN DVAR, prefix VArSa) — Discretionary

| Parameter | Unit | Range | Default |
| --- | --- | --- | --- |
| Operating status | – | 1 = Operating / 5 = Not-Operating | 5 |
| Feed-in / feed-out reactive power | % | 0..100 (+capacitive / -inductive, ref. Smax) | 0 / 0 |
| Activation command | – | 5 = Inactive / 1 = Active | 5 |
| Function status | – | 0 = Not available / 2 = Automatic (Priority) | 2 |

## 5.6 Fixed Power Factor — cosφ (Table 90 — LN DFPF, prefix PFSP)

| Parameter | Unit | Range | Default |
| --- | --- | --- | --- |
| Operating status | – | 1 = Operating / 5 = Not-Operating | 5 |
| Cosφ setpoint, generation | P.U. | -1.00..+1.00 (+cap / -ind) | -0.95 |
| Cosφ setpoint, absorption | P.U. | -1.00..1.00 (+cap / -ind) | 0.95 |
| Activation command | – | 5 = Inactive / 1 = Active | 5 |
| Function status | – | 0 = Not available / 1 = Autonomous / 2 = Automatic (Priority) | 1 |

## 5.7 Reactive Power Control, curve Q = f(V) (Table 91 — LN DVVR, prefix VArV)

| Parameter | Unit | Range | Reference | Default |
| --- | --- | --- | --- | --- |
| Operating status | – | 1 = Operating / 5 = Not-Operating | – | 5 |
| Activation command | – | 5 = Inactive / 1 = Active | – | 5 |
| Function status | – | 0 = Not avail. / 1 = Autonomous / 2 = Automatic (Priority) | – | 1 |
| K | – | -1.00..1.00 | – | 0 |
| Active power lock-in | P.U. | 0.00..max | Nominal active power | 0.20 |
| Active power lock-out | P.U. | 0.00..max | Nominal active power | 0.05 |
| V threshold, higher 1 | P.U. | 0.00..max | Nominal voltage at PdC | 1.08 |
| V threshold, lower 1 | P.U. | 0.00..max | Nominal voltage at PdC | 0.92 |
| V threshold, higher 2 | P.U. | 0.00..max | Nominal voltage at PdC | 1.10 |
| V threshold, lower 2 | P.U. | 0.00..max | Nominal voltage at PdC | 0.90 |

## 5.8 Reactive Power via cosφ(P) curve (Table 92 — LN DPFW, prefix PFW)

| Parameter | Unit | Range | Reference | Default |
| --- | --- | --- | --- | --- |
| Operating status | – | 1 = Operating / 5 = Not-Operating | – | 5 |
| Activation command | – | 5 = Inactive / 1 = Active | – | 5 |
| Function status | – | 0 = Not avail. / 1 = Autonomous / 2 = Automatic (Priority) | – | 1 |
| P value (point A) | P.U. | 0.00..max | Nominal active power | 0.20 |
| Cosφ value (point A) | P.U. | -1.00..-0.1 / +0.1..1.00 (+cap/-ind) | – | 1.00 |
| P value (point B) | P.U. | 0.00..max | Nominal active power | 0.50 |
| Cosφ value (point B) | P.U. | -1.00..-0.1 / +0.1..1.00 (+cap/-ind) | – | 1.00 |
| P value (point C) | P.U. | 0.00..max | Nominal active power | 1.00 |
| Cosφ value (point C) | P.U. | -1.00..-0.1 / +0.1..1.00 (+cap/-ind) | – | 0.95 |
| Voltage lock-in | P.U. | 1.00..1.10 | Nominal voltage at PdC | 1.05 |
| Voltage lock-out | P.U. | 0.90..1.00 | Nominal voltage at PdC | 0.98 |

Source (Annex T): T.3.1.4.1 – T.3.1.4.8; T.3.3.1.2 "Control Data Models".

# 6. IEC 61850 Data Model Structure (T.3.3.1)

| Element | Value |
| --- | --- |
| Namespace name | "(Tr) IEC 61850-CEI016:2022" |
| Namespace version / revision | 2022 / 1 |
| Namespace release date | 1-04-2022 |
| Logical Device | Single LD: LD_Plant (contains all Logical Nodes) |
| LN prefixes by plant section | Global (whole plant), St (storage), GenPV, GenWi, GenTer, GenIdr |
| Single Generating Unit (SGG) instances | Multi-instance, N = 1..99 |
| Mandatory associated attributes | q (quality) and t (timestamp), wherever required by IEC 61850 |

Presence-condition attribute values used throughout the CCI data tables (extension to standard M/O/C):

- M = Mandatory (prescribed by the standard).

- O = Optional (provided by the standard).

- C = Conditional (per standard-defined conditions).

- R = Required (standardized as O/C by IEC 61850, but required to enable Annex O functions).

- E = Extension (not present in the base standard, required for Annex O functions).

- F = Forbidden (not applicable for this presence condition).

Source (Annex T): T.3.3.1 "IEC 61850 data model of information associated with the CCI"; Table 94, Table 95, Table 96.

## 6.1 Key Logical Nodes Reference

| LN class | Typical prefix | Function |
| --- | --- | --- |
| LPHD1 | – | Physical device identity: PhyNam (vendor, swRev, location = POD identifier) |
| DPCC1/2/3 | PdC_Wi, PdC_Wa, PdC_Qi, PdC_Qc, PdC_VA | Nameplate power vector at PdC (§4) |
| DECP1 | DisFR | Overall plant readiness for control functions (Beh) |
| DGEN1 / DSTO1 | DisFR | Generation / storage macrogroup readiness for control |
| MMXU1 / MMXU2 | PdC, GenPV/Wi/Ter/Idr, St, SGG | Measurements (§3) |
| XCBR1 | IDG | Main power plant breaker position (Pos, Open/Closed) |
| DGEN2 | SSGG | Single Generating Unit operating status (Health) + ID (GnGrId), N=1..99 |
| DWMX1 / DAGC1 / DVAR1 / DFPF1 / DVVR1 / DPMC1 / DECP2 / DPFW1 | Wlim, WSd/WSa, VArSd/VArSa, PFSP, VArV, PFW | Control functions, §5 |

# 7. ACSI Services and Access Privileges (T.3.3.2 / T.3.3.4.3)

The IEC 61850 server shall implement, at minimum, the following ACSI service classes (IEC 61850-7-2), each mapped to a privilege:

| ACSI class | Services | Privilege |
| --- | --- | --- |
| Server / Association / LogicalDevice | GetServerDirectory, Release, Abort, GetLogicalDeviceDirectory | Listobjects |
| Logical Node | GetLogicalNodeDirectory, GetAllDataValues | Listobjects, Readvalues |
| Data Object | GetDataValues, SetDataValues, GetDataDirectory, GetDataDefinition | Readvalues, Control/config, Listobjects |
| DataSet | GetDataSetValues, GetDataSetDirectory (Set/Create/Delete NOT applicable) | Dataset |
| Buffered / Unbuffered Report Control Block | Report, GetBRCBValues/GetURCBValues (Set NOT applicable) | Reporting |

Two custom mandatory roles (IEC 62351-8) must be implemented in addition to the seven standard roles:

| Role | Role-ID | Revision | Privileges |
| --- | --- | --- | --- |
| DSO_OPERATOR | -1 | 1.0 | LISTOBJECTS, READVALUES, DATASET (read-only), REPORTING (write only for report enable), CONTROL + CONFIG on DSO-reserved Data Objects (Table 98) |
| AGGREGATOR_OPERATOR | -2 | 1.0 | Same structure, restricted to Aggregator-reserved Data Objects (Table 99) |

- Access token formats: profile A (X.509 public-key certificate extension) or profile B (X.509 attribute certificate) mandatory; profile C (JSON web token) and D (RADIUS) optional.

- Attribute Certificates (profile B / PMI): recommended short validity, < 24 h, to limit replay risk.

- Non-DSO/Aggregator authenticated subjects get privileges consistent only with their assigned role — no implicit escalation.

Source (Annex T): T.3.3.2 "ACSI services"; T.3.3.4.3 "Role Management"; Tables 97–102.

# 8. Cybersecurity Profile (T.3.3.4)

## 8.1 Time Synchronization (T.3.3.4.5)

| Parameter | Requirement |
| --- | --- |
| Time reference | UTC (Coordinated Universal Time) |
| Reference-time uncertainty | ≤ ± 100 ms |
| Max clock deviation between MMS/E2E association peers | 10 minutes — beyond this, the association SHALL fail |
| Network sync protocol | NTP, client, UDP port 123 |
| Secure variant | Mandatory: NTS (IETF RFC 8915), TLS-based authentication |
| Server redundancy | Redundant NTP architecture required, to protect against "fake ticker" servers (n false tickers tolerated ⇒ 2n+1 servers) |

## 8.2 Transport Profile — TLS (IEC 62351-3)

| Parameter | Requirement |
| --- | --- |
| Default TCP port (T-profile with TLS) | 3782 |
| Minimum TLS version | v1.2 |
| Mandatory cipher suites | TLS_RSA_WITH_AES_128_CBC_SHA256; TLS_DHE_RSA_WITH_AES_128_GCM_SHA256; TLS_ECDHE_ECDSA_WITH_AES_128_GCM_SHA256 |
| Also required, disabled by default | TLS_RSA_WITH_NULL_SHA256 (no encryption; explicit enable procedure required) |
| TLS renegotiation interval | Aligned to CRL update period (≥ half of it); never < 10 minutes |
| TLS session resumption | At least every 2 hours; shorter than renegotiation interval; aligned to CRL update |
| Root certificates (CAs) supported | ≥ 5 different |
| Max public-key certificate size | 8192 octets (must be handled at least up to this size) |
| CRL update frequency | ≤ 24 hours |
| OCSP response cache | ≤ 24 hours (active session not terminated solely for exceeding this) |

## 8.3 Cryptographic Algorithms and Key Lengths (T.3.3.4.1)

| Element | Requirement |
| --- | --- |
| RSA key length | Minimum 2048 bit (recommended ≥ 3072 bit) |
| ECDSA key length | Minimum 256 bit (recommended ≥ 384 bit) |
| Hash (digital signature / ICV) | SHA-256 |
| Digital signature algorithms | RSA-with-SHA256; ECDSA-with-SHA256 |
| Integrity check (MAC) | hmacWithSHA256 |
| Symmetric encryption | aes128-CBC / aes256-CBC; aes128-GCM / aes256-GCM (also give integrity+auth) |
| Diffie-Hellman groups | DH-14 (2048-bit, with RSA); ECDH: DH-23 (secp256r1) and DH-28 (brainpoolP256r1) |
| Application profile | End-to-End (E2E) security mandatory, per IEC 62351-4 (association + data-transfer phase) |

## 8.4 GOOSE Communication Security (T.3.3.4.2, informative)

- GOOSE confidentiality is not mandatory (latency constraints), but integrity/authentication is expected via extended PDU (Reserved1/Reserved2 fields), HMAC-SHA256 or AES-GMAC, truncatable to 128/256 bit.

- Group Key Management Protocol distributes current + next key with validity time references.

- StNum/SqNum of received PDUs should be checked to detect potential replay; a PDU with lower values than previously received should be discarded even if multipath communication could explain it.

## 8.5 PKI — Certificate & Key Lifecycle (T.3.3.4.9)

- CCI shall generate/receive new key pairs when: no key pair present at start-up; change of controllership/ownership; command from an authorised entity; or suspected private-key compromise.

- Enrolment protocol: at least one of SCEP (IETF RFC 8894, legacy pre-2015 versions excluded) or EST (IETF RFC 7030, over TLS 1.2+) shall be supported.

- Certificate validity checking: both CRL and OCSP (RFC 6960) methods shall be supported; a nonce is mandatory in OCSP requests to prevent replay.

- Trust Anchors required at minimum: DSO's CA, Administrative Domain's CA, Manufacturer's CA. Optional: firmware-update signing CA, Aggregator's CA, PKI-service TLS CA (e.g. for EST).

- Certificate revocation grounds: suspected private-key compromise (device or CA), changed entity affiliation, replaced public-key certificate, CCI decommissioning, withdrawn role/privilege, suspected Attribute Authority key compromise.

## 8.6 Secure Boot & Firmware Update (T.3.3.4.8)

- Trusted, phased secure boot sequence: each stage's validity verified before the next stage is installed/initialised.

- Firmware update procedure mandatory steps: (1) verify updating user's credentials/authorisation; (2) verify full integrity and authenticity of new firmware via digital signature against the manufacturer's certificate public key; (3) controlled deactivation of CCI functions during update; (4) log the update activity — the security data logger itself must never be erased by this procedure.

## 8.7 Security Event Logging (T.3.3.4.6)

| Parameter | Requirement |
| --- | --- |
| Storage model | Sequential circular buffer (FIFO), not deletable/modifiable |
| Minimum stored events before overwrite | 2048 events (per IEEE 1686:2013) |
| Remote transmission | Syslog, RFC 5424/5425, over TLS |
| SNMP alternative | SNMPv3 with TSM profile (RFC 5591) over TLS (RFC 6353); Syslog→SNMP mapping per RFC 5676 |
| Event severity categories | alarm (unauthorised activity) / error / notice (authorised activity) / warning (abnormal but not necessarily malicious) |

Event categories logged (non-exhaustive; full mnemonic tables in Annex T §T.3.3.4.6.2): login/logout and authentication outcomes; user/role/permission management; file hash & digital-signature check failures; software update outcome; TLS session and certificate-validation events (including expired/revoked/untrusted certificate, CRL/OCSP unavailable or expired); MMS association handshake failures (E2E SecPDU reject/abort with diagnostic code); certificate lifecycle events (enrolment, renewal, revocation, CertAVL); RBAC/access-token validation failures.

## 8.8 Traffic Segregation and Local Interface Security (T.3.3.4.10 / T.3.3.4.11)

- Remote-access segregation via router devices supporting NAT, VLAN, firewalling and VPN with channel encryption; any public-network connectivity must use a secure VPN, reserved exclusively for plant control/operation communications.

- All local (non-network) commissioning/configuration communication must be protected by a user-authentication system under specific security policies.

- User (non-DSO/Aggregator) remote access: standard protocols with confidentiality/authenticity/integrity (SSH or HTTPS), cryptographic credentials, mutual authentication; a segregation-of-duty role system limits access to CCI function/parameter subsets.

Source (Annex T): T.3.3.4.1 – T.3.3.4.11 in full; Tables accompanying each subclause.

# 9. Cross-Check Against Annex O Open Items

This section maps each open item listed in §13 of the companion Annex O document to where it is now resolved.

| Annex O open item | Resolved in this document |
| --- | --- |
| Complete IEC 61850 logical-node / data-model mapping for all measurements, signals and commands | §3 (measurements), §4 (nameplate vector), §5 (control functions), §6 (LN/LD structure) |
| Full cybersecurity architecture: PKI, authentication, Asset Inventory API | §8.5 (PKI/certificates), §7 (roles/ACSI), §8.7 (logging); Asset Inventory identified via LPHD.PhyNam (T.3.3.4.7) |
| GOOSE/MMS specific timing performance classes beyond O.7.3 | §2 (Type 3 = ~500 ms; Type 1 for GOOSE subscribe) |
| Detailed VPN/private-network requirements for Eth_A/Eth_B | §8.8 (traffic segregation: NAT/VLAN/firewall/VPN with channel encryption) |

Remaining gap: Annex T references a separate Technical Report "Example of SCL file for the IEC 61850 communication of CCI" for the concrete implementation of the CCI communication mode (§T.3.1). This SCL example has not been supplied and should be requested before finalising the IED configuration.

Together with the Annex O companion document, this file constitutes the complete mandatory-requirements baseline extracted from CEI 0-16 for the CCI AiLux firmware, as of the source publication date (2024-12).