# CCI (TG-500 / TG-524 / TG-525) — Hardware/Interface Protocol Reference

For each physical interface/component: (1) general communication protocols the hardware supports, per the TesPro datasheet, and (2) security requirements that apply — overwhelmingly IEC 62351 (each entry's heading names the specific part, e.g. “(62351-4)”), with one Annex O-only exception explicitly marked as such (USB local authentication). These are kept in separate columns — “supported by the vendor” and “mandated by a security requirement” are different kinds of claims. New protocols are added as extra lines within a row, not new columns.

| Hardware / Interface | Vendor-Supported Communication Protocols (TG-500 datasheet) | Security Requirements (IEC 62351; Annex O where noted) | Source / Notes |
| --- | --- | --- | --- |
| Eth_A (RJ45/optical, DSO channel) | - Network Protocols: TCP, UDP, HTTP, HTTPS, etc. [TG-500 datasheet] - Industrial Protocols: IEC 61850/MMS, Modbus TCP, OPC UA, PROFINET, EtherCAT [TG-500 datasheet, device-level] - IEC 60870-5-104 Slave/Reverse/Redundancy; IEC 61850 Server/Client/GOOSE; Modbus-TCP/IP Master/Slave; DNP3; S7-Comm; OPC-UA Client; C37.118 Client; IEC 62056-21 (DLMS/COSEM) - Physical layer: 100BaseFX, optical, dual LC connector, 1310nm multimode fibre [Annex O O.13.1.1.1] | IEC 61850/MMS security (62351-4) - Native mode → e2eMmsAC context [62351-4 §5.2] - Secure MMS = TCP port 3782 [62351-4 §6.3] - E2E handshake + data-transfer auth (ClearToken1/2/3) [62351-4 §13] TLS 1.2 transport security (62351-3) - Mandatory (RFC 5246) [62351-3 §5.2] - Mutual X.509 authentication [62351-3 §5.6.3] - RSA ≥2048 mandatory; ECDSA secp256r1 optional [62351-3 §5.6.4.6–7] PKI / certificates (62351-9) - IDevID → LDevID onboarding (802.1AR) [62351-9 §5.8] - ≥5 CA trust anchors [62351-9 §7.3.6] - Separate TLS vs E2E certs [62351-4 Annex G.2] Security event logging (62351-14) - TLS + E2E/MMS events [62351-14 Annex B.1.1/B.1.2] - Syslog over TCP/6514 + TLS mandatory, UDP prohibited [62351-14 §6.5] Zone/conduit architecture (62443-3-2) - Access point AP-1; Zone Z1 (DSO, external high trust) ↔ Conduit C1 ↔ Zone Z0 (CCI core) [62443 Zones doc] - SL-T = 2 proposed for Z0, Z1, C1 [62443 Zones doc] - C1 controls: firewall; no plant routing; IEC 62351-4 target [62443 Zones doc] | Annex O O.13.1.1.1 (interface); 62351-1/3/4/9/14 (security); TG-500 datasheet (comm protocols) |
| Eth_B (RJ45, other operators / BSP channel) | - Network Protocols: TCP, UDP, HTTP, HTTPS, etc. [TG-500 datasheet] - Same Ethernet protocol set as Eth_A available on this port - Physical layer: 10BaseT/100BaseTX, auto-negotiation, auto MDI/MDIX [Annex O O.13.1.1.1] | TLS 1.2 transport security (62351-3), conditional - Applies IF this channel uses TCP/IP + TLS — NOT mandated by CEI specifically for this channel [Annex O] PKI / certificates (62351-9) - Same CA trust store as Eth_A, if TLS used here too [inferred, not directly cited] Zone/conduit architecture (62443-3-2) - Access point AP-2; Zone Z2 (Operator, external medium trust) ↔ Conduit C2 ↔ Zone Z0 (CCI core) [62443 Zones doc] - SL-T = 2 proposed for Z2, C2; controls: firewall, Eth_B only [62443 Zones doc] | Annex O O.13.1.1.1 — no protocol mandated by name; left to producer's choice |
| RS-485 × 2, RS-232 × 1 (plant-element serial) | - Modbus RTU [TG-500 datasheet, field “Modbus”] - Meter Protocols: IEC1107, DLT645, DLMS [TG-500 datasheet] - Serial Port Protocols: Pass-through, TCP client/server, UDP, Modbus RTU gateway [TG-500 datasheet] - IEC 61158-15 Modbus-RTU; IEC 60870-5-101 (Balance and Unbalance); IEC 60870-5-103 [Ailux CCI manual] - Params: 1×RS232 + 2×RS485 (simultaneous); data bits 7/8; stop bits 1/2; parity None/Odd/Even; baud 300–230400 bps [TG-500 datasheet] - RS232 pinout (electrical/physical layer, EIA/TIA-232): terminals V/TX/RX/GND, DB9 2-RX/3-TX/5-GND [TG-500 datasheet] - RS485 pinout (electrical/physical layer, TIA/EIA-485-A): 2 independent buses — Bus 1: A1/B1/G; Bus 2: A2/B2/G [TG-500 datasheet; per-bus protocol assignment NOT specified in the 2-page datasheet — confirm against full TesPro manual whether both buses run the same protocol set or are assigned to different uses] - NOTE: RS-485/RS-232 themselves carry no protocol meaning — they are the physical/electrical layer only. The actual protocols riding on top (Modbus RTU, IEC 60870-5-101/-103, listed above) are what interpret the bytes. | IEC 62351-3 / -5 - Applies to IEC 60870-5-101/104 and DNP3 traffic on this bus [Ailux CCI manual, part–protocol mapping] Zone/conduit architecture (62443-3-2) - Access point AP-3; Zone Z3 (Plant, lower field trust) ↔ Conduit C3 ↔ Zone Z0 (CCI core) [62443 Zones doc] - SL-T = 1 proposed for Z3/C3 (lower than DSO/operator conduits) [62443 Zones doc] - C3 controls: RS485 isolation; master-poll only; no forwarding [62443 Zones doc] | Annex O O.13.1.4 (interface, generic); TG-500 datasheet + Ailux CCI manual (comm protocols) |
| CAN bus × 2 (independent, no interference) | - Bus standard: ISO 11898 [TG-500 datasheet] - Supported baud rate: 5 kbps – 1 Mbps; differential CANH/CANL 1.5–3.0V [TG-500 datasheet] - Operating modes: High-speed / Slope control / Standby low-power [TG-500 datasheet] - Networking capability: >110 connected nodes [TG-500 datasheet] - Industrial Protocols list includes CAN [TG-500 datasheet, device-level] | — not yet determined (to be filled) | TG-500 datasheet; no IEC 62351 part identified yet for this bus |
| USB 3.0 (local config console + plant elements) | - 1× USB port for local Configuration/Maintenance Console; 2× USB ports for plant-element connections | Local authentication (Annex O, NOT an IEC 62351 citation) - Technologies for recognising users required [Annex O O.13.1.1.2] - IP communication explicitly EXCLUDED on this port [Annex O O.13.1.1.2] PKI / credentials (62351-9, partial fit) - §5.8.1 proof-of-identity / proof-of-possession concept applies, though not written for local/serial ports specifically [62351-9] Zone/conduit architecture (62443-3-2) - Access point AP-4; Zone Z4 (Maintenance, temporary) ↔ Conduit C4 ↔ Zone Z0 (CCI core) [62443 Zones doc] - Separate zone per ZCR 3.4 (temporary devices kept apart from permanent IACS) [62443 Zones doc] - C4 controls: physical USB; RBAC; kept out of certification path where possible [62443 Zones doc] | Annex O O.13.1.1.2; no 62351 part directly cited for USB by Annex O |
| Wi-Fi 7 (BE5000, MT798X core) | - Wi-Fi 7 high-speed wireless backhaul [TG-500 datasheet, overview] | Zone/conduit architecture (62443-3-2) - Access point AP-6; explicitly listed as “Disabled in product profile” / “N/A (lab)” [62443 Zones doc] | TG-500 datasheet; not an interface named in Annex O O.13.1.1.x / O.13.1.4; the 62443 zones document explicitly states Wi-Fi is disabled in the product profile |
| TPM 2.0 (built-in security chip) | — none listed | PKI / key management (62351-9) - Private key protected in TPM/secure store; PKCS#12 mandatory [62351-9 §5.7.3.2/§7.3.2] - RNG per ISO/IEC 18031; TPM/TRNG as OOB seed source [62351-9 §6.4] Certificates, dual profile (62351-4 Annex G) - Separate end-entity certs for TLS vs E2E, both TPM-backed [62351-4 Annex G.2] - Cert ≤8192 octets; RSA≥2048/EC≥256 [62351-4 Annex G.3–G.4] RBAC access tokens (62351-8) - Three token profiles: A = X.509 ID certificate + extension; B = X.509 attribute certificate; C = software token (no asymmetric crypto, Kerberos-like) [62351-8 §9.2] - IECUserRoles OID extension: id-IEC62351={1 2 840 10070}; access token OID = 1.2.840.10070.8.1 [62351-8 §9.3] - Mandatory token fields: serial number, subject/holder name, assigned role, issuer, timestamp, validity period, revision number [62351-8 §9.4.1] - RoleID: INTEGER(-32768..32767); positive values reserved for IEC 62351; negative values for private/other-standard usage (e.g. IEEE 1815) [62351-8 §9.4.4.1] RBAC mandatory algorithms (62351-8) - Hash: SHA-1 mandatory (backward compat only) + SHA-256 mandatory (preferred) [62351-8 §9.5.1.3] - Signature: RSA 1024-bit mandatory (backward compat) + RSA 2048-bit mandatory (preferred); ECDSA/ECGDSA optional, min. 192-bit (with SHA-1) or 256-bit (with SHA-256) [62351-8 §9.5.1.3] - NOTE: RSA-1024 being still “mandatory” (for backward compatibility) differs from 62351-3's stricter “1024 deprecated” rule — worth flagging as a cross-part inconsistency to confirm with the team RBAC session/message-based auth (62351-8) - Session-based: one-time auth via Diffie-Hellman key agreement; subsequent messages integrity-protected via HMAC-SHA256 using the shared secret [62351-8 §8.2, Figure 6] - Message-based: access token + digital signature applied to every single message individually; supports multi-source aggregation via a substation controller acting as data concentrator [62351-8 §8.3] RBAC verification & PKI mapping (62351-8) - Subject must be authenticated (“secure” per 62351-5 definition) before an access token can be used [62351-8 §11.1.2] - Profile A is part of a PKI; Profile B is a PMI interconnected with a PKI; Profile C is Kerberos-like, a PKI may underlie the software-token repository [62351-8 §12.5] Security event logging (62351-14) - Full PKI event catalogue: enrolment, cert validation, revocation [62351-14 Annex B.1.6, Tables 33–37] | TG-500 datasheet (TPM2.0 confirmed, Trust Zone + Secure Boot also confirmed); Annex O O.13.7 / O.15.3 (FIPS 140-2 L3) — functional requirements only; 62351-8 content re-verified from a clean 53-page screenshot capture (not OCR) |
| GNSS/GPS receiver (GPS, GLONASS, BDS, Galileo, QZSS opt.) | — none listed | Time synchronization (62351-4, -9) - 10-min UTC clock-skew tolerance for MMS auth; duplicate time → P-ABORT [62351-4 §11.2.3–4] - UTC format YYYYMMDDhhmmss,sssZ, no 'T' separator [62351-4 §13.1.2] - Clock sync mandatory for cert validity checks; PTP 1588v2.1 or NTS recommended [62351-9 §7.7 / Table 6 A-14] Security event logging (62351-14) - Optional timeQuality SD-ELEMENT when GNSS/NTP trust is uncertain [62351-14 §6.2.2 Table 6] | TG-500 datasheet; Annex O O.13.5 (UTC sync, ±100ms) |
| Cellular modem (TG-524: 4G / TG-525: 5G) | - 2G GSM/EDGE: bands B2/B3/5/8 [TG-500 datasheet] - 3G WCDMA: B1/2/4/5/6/8/19 [TG-500 datasheet] - 4G LTE-FDD: B1/2/3/4/5/7/8/12/13/18/19/20/25/26/28; LTE-TDD: B38/39/40/41 [TG-500 datasheet] - Cellular class: 4G Cat 1 / 4G Cat 4 (TG-524); 5G RedCap / 5G SA (TG-525) [TG-500 datasheet] - Dual SIM card slots [TG-500 datasheet] - Device-level: IEC 61850/MMS, Modbus TCP/RTU, OPC UA also listed as supported access protocols [TG-500 datasheet overview — not confirmed whether these ride specifically over cellular or only over Ethernet] | TLS 1.2 transport security (62351-3), conditional - Applies to whatever TCP/IP traffic rides over the cellular data link — same rules as Eth_A/B if this link carries CCI application data [inferred from 62351-3 general applicability] Zone/conduit architecture (62443-3-2) - Access point AP-5; Zone Z5 (External backup WAN) ↔ Conduit C5 ↔ Zone Z0 (CCI core) [62443 Zones doc] - Kept separate per ZCR 3.6; C5 controls: IP/VPN, NO Layer-2 bridge to Eth_A, default deny [62443 Zones doc] | TG-500 datasheet; no CEI 0-16 clause specifically regulates the cellular link itself (confirmed by full-text search of Annex T) |

# System-Wide Functional, Performance & Operational Requirements

These requirements apply to CCI as a whole rather than to one specific hardware interface, so they don't fit the per-interface table above. Same sourcing standard: every line is cited to its clause.

| Category | Requirement(s) |
| --- | --- |
| Timing & control dynamics | - Fast control ring settling times: TsP ≤ 60s (active power), TsQ ≤ 10s (reactive power) [Annex O O.7.3.1] - Slow control ring cycle time ΔT: adjustable 10s–600s [Annex O O.7.3.2] - External set-point updates: minimum 3s interval between accepted updates; faster updates rejected [Annex O O.7.3.3] - Measurement reference: fixed block interval method per IEC 61557-12; fast ring uses 200ms blocks (M_C200), slow ring uses ΔT blocks (M_CΔT); voltage/current sampled synchronously [Annex O O.7.4] |
| Measurement accuracy | - Accuracy class per measurement converter, per IEC 61557-12 classes defined in O.13.2.1 [Annex O O.13.2] - Must satisfy Tables 5 and 6 accuracy requirements of TSO Grid Code Annex A.6 (or demonstrably congruent alternative) [Annex O O.13.2] |
| Power supply | - CCI and associated communication equipment powered from an auxiliary voltage source; availability guaranteed by UPS or battery backup for at least 1 hour [Annex O O.13.3] - 12–36V DC wide-range input [TG-500 datasheet] |
| Firmware/software update | - Dedicated update procedure required, to correct errors/vulnerabilities [Annex O O.13.4] - Procedure shall: disable CCI functionality in a controlled manner during update; verify firmware digital signature/integrity via manufacturer certificate before applying [Annex O O.13.4] - Update activity (including version, and any failed updates) shall be recorded in the data logger; no step may delete existing log data [Annex O O.13.4] |
| Self-diagnostics | - CCI shall detect and report malfunctions in itself or at its interconnection interfaces, including loss of communication [Annex O O.13.6] - On self-diagnostic detection of an out-of-service condition, an alarm shall be raised and recorded in the data logger with available diagnostic detail [Annex O O.13.6] |
| Asset inventory | - CCI shall interface with an Asset Inventory infrastructure as indicated in Annex T [Annex O O.13.7.2] |
| Data logger (event storage) | - Verifies and records: CCI power presence; comms to DSO/external operators/plant elements (physical+data link); CCI functionality; measurement device functionality [Annex O O.14] - Also stored: DG/DI switch status; power on/off + cause; firmware update (version) incl. failures; irregular network connect/disconnect; abnormal service-endpoint connections; anomalous traffic fingerprint (port/deep scanning); malformed messages/authenticity failures; failed AND successful authentications; system time changes; unsuccessful/successful key-credential modification; alarm/error log resets [Annex O O.14] - If bootloader lockout password used: failed + successful boot authentication also stored [Annex O O.14] - Also: control function start/stop/activation status; commands issued to plant elements + trigger event; DSO commands w/ parameters; other authorised operator commands; PG/PI protection tripping; teletripping (defence plan) tripping; over/under-frequency regulation tripping [Annex O O.14] - Minimum 2048 events, non-overwritable by user, timestamped (yyyy/mm/dd hh:mm:ss); exportable via manufacturer-supplied interface [Annex O O.14] - Access protected by username/password [Annex O O.14] - Remote reading via standard protocol — e.g. SIEM via syslog, per RFC 5424 [Annex O O.14] |
| Testing & certification | - Three test categories: functional (O.15.1), general conformity (O.15.2), cybersecurity (O.15.3) [Annex O O.15] - Functional tests verify: measurement accuracy/disturbance immunity/update intervals; IEC 61850 communication correctness (per Annex T); self-diagnostics; data logging; regulation/control output consistency in both autonomous and slaved mode; correct fallback to default function on timeout/comms loss [Annex O O.15.1] - General conformity per CEI EN 61557-12; reference temperature class no lower than K55; PMD-A qualification not required [Annex O O.15.2] - Hardware cybersecurity: minimum Level 3 tamper resistance, certified via FIPS 140-2 by an independent entity [Annex O O.15.3] - CE marking required; compliance attested via manufacturer self-certified Declaration of Conformity [Annex O O.15.4] - Operating temperature: -5°C to +45°C (Ailux CCI) / -40°C to +75°C (TG-500) — both meet the K55 minimum class [TG-500 datasheet] |
| Services (device-level) | - http(s), sftp, ssh, SNMP v2/v3 trap - ntpd; client-PTP or server-PTP (IEEE-1588, power profile) - Redundancy cover system; firewall; RBAC-protected access - IEC 61131-3 ladder logic tasks - Web interface for diagnostics, log management, SCADA |
| Digital I/O | - 5× optoisolated digital inputs, 10–120 Vdc, externally powered by field supply - 3× relay digital outputs, 250 Vac / 3A - TG-500 variant: 2× DI, 2× DO (8-P socket) [TG-500 datasheet] - NOTE: DI/DO carries no communication protocol — it's a raw electrical on/off signal, read directly by CCI's own software (no framing, addressing, or handshake). - Governing requirements instead: switch/DG-DI status changes must be detected and reported within 4s of the event [Annex O O.8.6] - DG/DI switch status changes must be recorded in the data logger [Annex O O.14] |

Source documents: TG-500 Series Technical Datasheet (TesPro, re-extracted directly from PDF for this update — confirms TG-524 = 4G variant, TG-525 = 5G variant of the same series); user-supplied IEC 62351 extracts (parts 1, 3, 4, 9, 14, +8 lower confidence); CEI 0-16 Annex O and Annex T (full text).

The “Vendor-Supported Communication Protocols” column lists what the hardware CAN do per the manufacturer — it is NOT a security requirement and should not be read as one. The “IEC 62351 Security Requirement(s)” column is the only column reflecting mandatory/normative clauses.

Device-level protocols (IEC 61850/MMS, Modbus TCP/RTU, OPC UA) are listed in the datasheet's overview without specifying which physical interface(s) carry them — attributed here to Eth_A/Eth_B (most likely, matching Annex O's IEC 61850 requirement) and flagged separately under the cellular row since the overview groups them near the connectivity description; this attribution should be confirmed against the full TesPro manual, not assumed.

62351-8 (RBAC) content was re-extracted from a clean, 53-page screenshot capture of the real IEC TS 62351-8:2011(E) document (pages covering §4.2, §8.2–8.3, §9 access token definitions, §11 verification, §12.5 PKI mapping, Figure 3 and Figure 6) — this REPLACES the earlier “OCR-sourced, lower confidence” placeholder with directly-read, clause-cited content. One cross-part inconsistency was found and flagged: 62351-8 §9.5.1.3 keeps RSA-1024 as “mandatory (backward compatibility)” for access-token signatures, while 62351-3 §5.6.4.6–7 calls RSA-1024 “deprecated” for TLS certificates — worth confirming with the team which rule governs where these two overlap.

# IEC 62443 — Zone/Conduit Architecture & Component Security

## Zone table (SL-T = target security level)

| Zone | Name | Assets | SL-T | Trust level |
| --- | --- | --- | --- | --- |
| Z0 | CCI core | TG-524/TG-500, CCI firmware, TPM | SL 2 | Highest internal trust |
| Z1 | DSO | DSO head-end, remote clients (via Eth_A) | SL 2 (conduit C1) | External, high trust |
| Z2 | Operator | Qualified operator SCADA (via Eth_B) | SL 2 (conduit C2) | External, medium trust |
| Z3 | Plant | Analyzers, inverters, RTU (via RS-485) | SL 1 (conduit C3) | Field, lower trust |
| Z4 | Maintenance | USB console laptop | Separate (ZCR 3.4) | Temporary access only |
| Z5 | Backup WAN | LTE modem path | Separate (ZCR 3.6) | External, no L2 bridge to Z1 |

## Conduit table

| Conduit | Path | Protocols | Controls |
| --- | --- | --- | --- |
| C1 | Z1 ↔ Z0 (Eth_A) | IEC 61850 MMS, GOOSE (62351-TLS target) | Firewall; no plant routing; IEC 62351-4 target |
| C2 | Z2 ↔ Z0 (Eth_B) | IEC 60870-5-104, 61850 client | Firewall; Eth_B only |
| C3 | Z3 ↔ Z0 (RS-485) | Modbus RTU/TCP | RS-485 isolation; master-poll only; no forwarding |
| C4 | Z4 ↔ Z0 (USB) | SSH/HTTP console (TBD) | Physical USB; RBAC; kept out of cert path where possible |
| C5 | Z5 ↔ Z0 (LTE/WAN) | IP/VPN | NO Layer-2 bridge to Eth_A; default deny |

## Component & process requirements summary

62443-3-3 (System security requirements, SL-C): 7 Foundational Requirements — FR1 Identification & Authentication Control (incl. SR1.8 PKI certificates), FR2 Use Control, FR3 System Integrity, FR4 Data Confidentiality, FR5 Restricted Data Flow, FR6 Timely Response to Events, FR7 Resource Availability. Target: SL-C 2 for Z0 (CCI core), matching the SL-T 2 proposed at the zone level.

62443-4-1 (Secure Development Lifecycle, process/audit basis): 8 Practices — Security Management (SM), Specification of Security Requirements (SR), Secure by Design (SD), Secure Implementation (SI), Security Verification & Validation Testing (SVV), Management of Security-Related Issues (DM), Security Update Management (SUM), Security Guidelines (SG). Applies to HiTEKS/TesPro as product supplier, not the DSO/integrator. Target maturity: ML 2–3 for first certification pass.

62443-4-2 (Component technical requirements, CR/RE): TG-524/TG-500 CCI is primarily an Embedded Device (EDR, §13) + Software Application (SAR, §12), with partial Network Device requirements (NDR, §15) for the firewall/LTE zone boundary. Adds CR1.14 (symmetric key mgmt), CR2.13 (physical diagnostics), CR3.10–14 (secure updates, tamper protection, root of trust, secure boot) — the last three connect directly to the TPM 2.0 / secure boot work in the hardware table above.

Explicit vendor conformance claim: “Conforme a quanto previsto da IEC-62443-4-1/2”.

# Notes

IEC 62443 is now integrated (Zones, 3-3, 4-1, 4-2) — both as the dedicated architecture section above and as “Zone/conduit architecture” entries cross-referenced into each relevant hardware row in the main table (Eth_A→Z1/C1, Eth_B→Z2/C2, RS-485→Z3/C3, USB→Z4/C4, LTE→Z5/C5, Wi-Fi→disabled). Source material for 62443 is marked in the original documents as partial captures (screenshot-based, some sections still gaps) — treat as a solid working map, not a fully verified word-for-word citation the way the 62351-8 re-extraction was.