AiLux CCI – Controllore Centrale di Impianto

Mandatory Measurements, Timing Requirements and Technical Parameters

Extracted and consolidated from CEI 0-16:2022-03, Annex O ("DER Plant Controller")

Source document: Estratto CEI 0-16 – Allegato O (English translation, CT 316), publication date 2024-12

Status: PARTIAL — based on Annex O only. Annex T ("Cybersecurity requirements for communication"), which defines the full IEC 61850 data model, GOOSE/MMS timing and detailed cybersecurity parameters, has not yet been incorporated and will be added in a follow-up revision once available.

# 1. Purpose and Scope of This Document

This document consolidates every mandatory numerical requirement stated in Annex O of CEI 0-16:2022-03 ("DER Plant Controller" / CCI) that the CCI AiLux firmware and hardware must respect: control-loop timing, measurement periodicity, measurement accuracy classes, control-function parameters/thresholds, communication interface specifications, data-logging minimums, and certification requirements.

Values are grouped by functional performance category as defined by Annex O:

- PF1 — Mandatory: monitoring and data-exchange functions (always required).

- PF2 — Optional: voltage control and active power limitation at the POC (required in the manner/timeframe set by ARERA; already implemented as real functions in the CCI AiLux product).

- PF3 — Discretionary: plant management and Dispatching Services Market (MSD) participation.

Unless noted otherwise, every timing/accuracy value below is a hard normative requirement ("shall"), not a design suggestion.

# 2. Applicability Thresholds (Annex O, Clause O.2)

| Parameter | Value / Condition |
| --- | --- |
| Minimum total rated power for mandatory CCI (new connections, "standard perimeter") | ≥ 1000 kW (sum of production + storage units) |
| Plants participating in dispatching services | CCI required regardless of total power |
| Plants < 1 MW ("extended perimeter") / retrofits | Conditions to be established by ARERA (not yet fixed) |

Source (Annex O): O.2 "Scope".

# 3. Control-Loop Timing Requirements

CCI implements two nested control rings: the fast ("plant control") ring and the slow ("control curve analysis") ring. Both have normatively fixed timing.

## 3.1 Fast Control Ring (Plant Control Ring)

| Parameter | Requirement |
| --- | --- |
| Max settling time, active power (TsP) | 60 s, for any size of internal active-power set-point change |
| Max settling time, reactive power (TsQ) | 10 s, for any size of internal reactive-power set-point change |
| Settling-time definition | Time from instant of new set-point application to the instant the controlled quantity at POC (V, P, Q, etc.) stably enters a tolerance band of ±5% of the expected value |
| Measurement basis | MC200 — 200 ms fixed block interval measurements per IEC 61557-12 Annex B |
| Faster-than-required performance | Permitted (CCI may reach the expected value faster than the stated maxima) |
| MSD secondary power control (if participating) | Settling time must additionally allow the plant to follow the gradient prescribed by the TSO Grid Code |

Source (Annex O): O.7.3.1 "Dynamics of the fast control ring"; O.7.4.

## 3.2 Slow Control Ring (Control Curve Analysis Ring)

| Parameter | Requirement |
| --- | --- |
| Cycle time ΔT — adjustable range | 10 s to 600 s (settable operating parameter) |
| Cycle time ΔT — default value | 60 s, unless otherwise set by DSO in the "Operating Rule" |
| Reaction to external command changing control function/parameters | New parameters and control curves must be acquired and processed within ΔT of command reception |
| Minimum interval between change commands | Commands arriving at intervals shorter than ΔT are rejected |
| Measurement basis | MCΔT — measurements aggregated over the ΔT interval, per IEC 61557-12 Annex B |
| Voltage/current sampling | Voltage and current samples must be synchronous |

Source (Annex O): O.7.3.2 "Dynamics of the slow control ring"; O.7.4.

## 3.3 External Set-Point Command Dynamics

| Parameter | Requirement |
| --- | --- |
| Minimum interval between processed external set-point updates | 3 s |
| Commands arriving faster than 3 s | Rejected |

Source (Annex O): O.7.3.3 "External Set Point Dynamics".

# 4. Measurement & Data-Exchange Periodicity (Mandatory, PF1)

All periodic transmissions below must be synchronised to the 0/4/8/12/…/56-second marks of each minute (i.e., every 4 s, boundary-aligned).

| Data / Function | Aggregation window | Transmission periodicity | Notes |
| --- | --- | --- | --- |
| P, Q, V at POC → DSO (power-flow monitoring) | 4 s fixed block interval (IEC 61557-12) | Every 4 s, synchronous with :00,:04,:08… | Complete with timestamp and quality index (O.8.3) |
| P, Q at POC + aggregated/unit-level P → TSO via DSO (network observability) | 4 s | Every 4 s, synchronous with :00,:04,:08… | Overwrites previous value; no buffering at the interface (O.8.4) |
| Instantaneous P (and Q) at POC → Aggregator/BSP (MSD participation, PF3) | Instantaneous | Every 4 s, synchronous with :00,:04,:08… | Real-time value, not averaged (O.8.5) |
| Status change of General Switch (DG) / Generating-Unit Switch (DDG) | Event-driven | Notified within max 4 s of event occurrence | O.8.6 |

## 4.1 Generating-Unit-Level Measurement Thresholds (for individually transmitted P measurements)

| Unit type | Size threshold requiring individual measurement |
| --- | --- |
| Inverters of generating units (incl. wind via inverter) | Nominal power P ≥ 170 kW |
| Inverters of storage systems | Rated power P ≥ 50 kW |
| Rotating generators | Rated power P ≥ 250 kW |

Source (Annex O): O.8.4, item c).

# 5. Measurement Accuracy Requirements

| Element | Requirement |
| --- | --- |
| Measuring converter accuracy class | ≤ 0.2 |
| Current transformer (CT) accuracy class | ≤ 0.5 |
| Voltage transformer (VT) accuracy class | ≤ 0.5 |
| Rated burden (where applicable) | 5 VA or 10 VA |
| Measurement standard / method | IEC 61557-12, fixed block interval method (Annex B); accuracy classes as above |
| Dedicated fiscal-metering CT/VT reuse | Excluded — fiscal CTs/VTs cannot be used for CCI measurements |
| Shared transducers (measurement/protection) | Allowed only if no interference between uses (dedicated windings/cores if necessary) |
| Compliance target | Must satisfy accuracy requirements of Tables 5 & 6, Annex A.6 of the TSO Grid Code |

Source (Annex O): O.13.2.1 "Requirements for transducers and measuring converters".

# 6. Polygonal Characteristic & Power Reference Quantities (PF2/PF3)

Producer-declared quantities (stated in the "Operating Rule") that define the plant's operating envelope at the POC:

| Symbol | Meaning |
| --- | --- |
| Pass | Maximum active power absorption from the grid |
| Pimm (Pfed) | Maximum active power fed into the grid |
| Qcap | Maximum capacitive reactive power (overexcitation) |
| Qind | Maximum inductive reactive power (underexcitation) |
| Smax | Maximum apparent power = √[max(Pimm², Pass²) + max(Qind², Qcap²)] — used as the p.u. reference base for all set-points exchanged with DSO/Aggregator |

Source (Annex O): O.8.2 "Polygonal characteristic of the plant".

# 7. Control-Function Parameters and Thresholds (PF2 — Voltage Control & Active Power Limitation)

## 7.1 cosφ = f(P) Control (O.9.1.2)

| Parameter | Value |
| --- | --- |
| Deadband δcosφ (α) | α = 0.02 (default; must be adjustable) |
| Trigger rule | New cosφ transmitted to fast control ring only if ¦cosφ_calculated − cosφ_internal_setpoint¦ ≥ α |
| Voltage lock-in / lock-out thresholds | User-settable; verified on ΔT-averaged voltage |
| Recalculation rate | Every ΔT (slow control ring) |

## 7.2 Q = f(V) Control (O.9.1.3)

| Parameter | Value |
| --- | --- |
| Deadband δQ (σ) | σ = 5% of Qmax (default; must be adjustable) |
| Trigger rule | New Q transmitted to fast control ring only if ¦Q_calculated − Q_internal_setpoint¦ ≥ σ |
| Active-power lock-in threshold | 0.2 × Pfed |
| Active-power lock-out threshold | 0.05 × Pfed |
| Lock-in/lock-out verification basis | ΔT-averaged active power values |
| Voltage breakpoints (settable) | V1i, V2i, V1s, V2s (curve shape per CEI 0-16 Fig. 67 / Clause I.3) |
| Slope parameter k | Adjustable, −1 ≤ k ≤ +1 |
| Recalculation rate | Every ΔT (slow control ring) |

## 7.3 Active Power Limitation (O.9.2)

| Case | Requirement |
| --- | --- |
| Limitation for V ≈ 110% Un (O.9.2.1) | Autonomous function, user-activated only (local or remote terminal); every activation and every actual intervention must be logged in the data logger |
| Limitation on external DSO command (O.9.2.2) | Slaved function; if no comms channel, executed manually by user per the "Operating Rule" procedure |
| Modulation of active power on external DSO command (O.9.2.3) | Slaved function; identical implementation to the Active Power Set-Point function (O.10.3.1) |
| Max limitation step | Never larger than the steps stated in CEI 0-16 itself |

## 7.4 Plant Start-Up / Reconnection Power Gradient (PF3, O.10.1–O.10.2)

| Parameter | Value |
| --- | --- |
| Centralised start-up power growth gradient | Positive gradient not exceeding 20% Pn/min |
| Reconnection after interface-protection trip | Same gradient rule; reconnection enabled only once grid V/f meet CEI 0-16 clause 8.8.7.2 conditions |

# 8. Priority Among Control Functions (Table 1, Annex O Clause O.11)

Lower index = higher execution priority. If a higher/equal-priority function is requested while an incompatible lower-priority one is active, the new one takes over immediately.

| Priority index | Control function |
| --- | --- |
| 1 (highest) | Active power limit intervention for V ≈ 110% VN (O.9.2.1) |
| 2 | Active power limitation on external DSO command (O.9.2.2) |
| 3 | Modulation of active power to POC on external command from DSO (O.9.2.3) |
| 4 | Active Power Set-Point function on external command (O.10.3.1) |
| 5 | Voltage regulation via reactive power supply on external command from DSO (O.9.1.4) |
| 6 | Set-point power factor (cosφ) (O.9.1.1) |
| 6 | Reactive power control Q = f(V) (O.9.1.3) |
| 6 | Reactive power control cosφ = f(P) (O.9.1.2) |
| 7 (lowest) | Reactive Power Set-Point function on external command (O.10.3.2) |

Above/outside this table, with absolute priority over everything else: (a) individual-machine over-/under-frequency active-power regulation (CEI 0-16 §8.8.6.3.2 / §8.8.6.3.3 — explicitly NOT implemented by CCI itself, must remain at unit level); (b) full/partial plant disconnection commanded by the "defence plan" teletripping device (Annex M) — CCI must not take any conflicting action when this occurs.

# 9. Communication Interface Technical Specifications

## 9.1 External Network Interfaces (O.13.1.1.1)

| Interface | Purpose | Physical layer | Protocols |
| --- | --- | --- | --- |
| Eth_A | Communication to DSO | 100BaseFX, optical, dual LC connector, 1310 nm multimode fibre | TCP/IPv4 (mandatory), IPv6 (optional); IEC 61850 family (MMS, GOOSE); SSL/TLS 1.2+ per IEC 62351-4/-8/-9; DHCP; DNS forwarding |
| Eth_B | Communication to other enabled remote operators (User remote / Aggregator) | 10BaseT / 100BaseTX, auto-negotiation, auto MDI/MDIX (may use SFP) | Same protocol stack as Eth_A |

Both interfaces: physical-link and data-link status must be exposed in the data logger. No internal switch/bridge function is permitted between CCI's own interfaces — no data exchange between Eth_A, Eth_B, the local configuration port, or the plant-element network is allowed inside CCI.

## 9.2 Local Configuration / Maintenance Interface (O.13.1.1.2)

- Serial or USB technology only — IP-based communication explicitly excluded for security reasons.

- Must implement user-recognition/authentication to prevent unauthorised access.

## 9.3 Loss-of-Communication Fallback Timing (O.13.1.2 / O.13.1.3)

| Channel | Fallback behaviour |
| --- | --- |
| DSO channel (Eth_A) lost while CCI performs control | Automatic switch to pre-configured autonomous mode; switch delay must be long enough to ensure the loss is permanent (exact value set with DSO in "Operating Rule"); auto-restore to DSO-requested mode when comms return |
| Aggregator/BSP channel (Eth_B, MSD) lost | Same principle: delayed automatic switch to pre-configured mode, agreed with Aggregator after verification with DSO; auto-restore when comms return |

# 10. Power Supply, Clock and Reliability

| Parameter | Requirement |
| --- | --- |
| Backup power autonomy (UPS/battery) | ≥ 1 hour for CCI circuits and associated data-communication equipment |
| Time reference | UTC (Coordinated Universal Time), via GPS receiver |
| Time-sync uncertainty | ≤ ±100 ms |
| Clock drift during loss of external sync / power loss | ≤ 1 s/day, across the full allowable operating temperature range |
| Reliability/availability target | Per TSO Grid Code Annex A.13, Article 6.2 (subject to be defined per ARERA Resolution 628/18/R/EEL) |

Source (Annex O): O.13.3 "CCI Power supply"; O.13.5 "Internal clock and synchronisation"; O.13.10.

# 11. Data Logger Requirements (O.14)

| Parameter | Requirement |
| --- | --- |
| Minimum stored events (rolling, non-overwritable by user) | 2048 events |
| Timestamp format | yyyy/mm/dd hh:mm:ss |
| Access control | Username/password (or equivalent) required |
| Remote read-out | Standard protocol (e.g., syslog per RFC 5424, for SIEM integration) |

### Mandatory event categories to be logged

- CCI power supply presence; power on/off and cause; firmware update (incl. version) and failed updates

- Status (open/closed) of General Switch (DG) and Interface Switch(es) (DI)

- Presence/absence of communication to DSO, to external operators, and to plant elements (physical-link and data-link status)

- CCI functionality status; measurement-device functionality status

- Irregular connections/disconnections to the communication network; connection to abnormal service endpoints or at inappropriate times

- Anomalous network-traffic fingerprints (port scanning, deep scanning, etc.); malformed messages / message-authenticity verification errors

- Authentication attempts (failed and successful); credential/key changes and failed change attempts; alarm/error-log resets

- If bootloader lockout password is used: failed and successful boot authentications

- Start/stop/activation status of each control function; events causing CCI to issue commands to plant elements (e.g. exceeding 110% Vn threshold, control-function intervention, set-point implementation)

- Commands received from DSO and from any other authorised external operator, with their parameters

- Tripping of General Protection (PG) and Interface Protection (PI)

- Tripping of the defence-plan teletripping function (Annex M)

- Tripping of over-/under-frequency regulation by controlled machines/units

- Any change to control-function priority settings

- Entry of new/changed characteristic electrical parameters of the installation (polygonal curve updates)

# 12. Testing, Accreditation & Certification Requirements

| Test category | Requirement / Standard |
| --- | --- |
| Functional tests | Verify all applicable PF1/PF2/PF3 functions per Annex O Clause O.6; measurement accuracy, disturbance immunity, update-interval compliance; IEC 61850 comms correctness; self-diagnostics; data logging |
| General conformity (environmental/EMC/insulation) | CEI EN 61557-12 (recalls IEC 61010-1 and, notably, IEC 61010-2-201); reference temperature class ≥ K55; must run in a lab accredited per CEI UNI EN ISO/IEC 17025 (in Italy: ACCREDIA) |
| Hardware cybersecurity / tamper resistance | At least FIPS 140-2 Level 3, certified by an independent body |
| Product security (secure development lifecycle) | ISA Secure EDSA v3.0.0, per IEC 62443-4-1 and IEC 62443-4-2 |
| IEC 61850 conformance | Certified by a laboratory accredited by the UCA User Group |
| Secure transport (IEC 62351-3) | Conformance per IEC 62351-100-3, certified by an accredited body |
| Quality system | ISO 9001:2000 (as amended) certification of the manufacturing process |
| CE marking | Mandatory |
| Declaration of Conformity | Manufacturer self-certification per Art. 47 of Italian Presidential Decree 445/2000; test reports retained ≥ 20 years from last production |

# 13. Open Items — Pending Annex T

The following items are referenced by Annex O but fully specified only in Annex T ("Cybersecurity requirements relating to communication from the outside to CCI and from CCI to the outside"), which has not yet been uploaded/processed:

- Complete IEC 61850 logical-node / data-model mapping for all measurements, signals and commands listed in this document (Appendix O-1 gives only illustrative examples, e.g. Q=f(V) status transitions OFF→ON→ACT).

- Full cybersecurity architecture: certificate/PKI management, authentication mechanisms referenced in O.13.4 (firmware update) and O.13.7 (hardware tamper protection), Asset Inventory API details (O.13.7.2).

- GOOSE/MMS specific timing performance classes, if any beyond what O.7.3 already fixes.

- Detailed VPN/private-network requirements for Eth_A/Eth_B referenced in Annex O footnote 197.

Once Annex T is available, this document should be revised to add a dedicated "Cybersecurity & Data Model" section and cross-check every mandatory value above against Annex T for consistency.