# Figura 2 (PF2) — Parameters, equations & CCLI mapping

Document ID: CCLI-LAB-FIG2-PAR-001  |  Rev 1.0  |  2026-09-22
Sources: CEI TR 57-126 §6.2 Table 1 · CEI 0-16 Allegato O/T · CCLI apps/ccli/core/dso/ · lab/CCI_Figura2_Parameters.md

# Table numbering (Italian consolidated vs English extract)

| Function | Italian Allegato T | English CCI_Annex_T_Extract §5 |
| --- | --- | --- |
| Wlim (O.9.2.2) | Tab. 84 | Table 85 |
| WSd (O.9.2.3) | Tab. 85 | Table 86 |
| WSa (MSD) | Tab. 86 | Table 87 |

# 1. Figura 2 use case (TR Table 1 — ON/OFF)

| Function | TR state | Clause | Figura 2 |
| --- | --- | --- | --- |
| Wlim | Not operative / Inactive | O.9.2.2 | Off |
| WSd | Operative / Active | O.9.2.3 | On — green s.p. W |
| WSptPct | +20 % Smax | O.9.2.3 | Export set-point |
| VArSd, PFSP, VArV, PFW | Not operative | O.9.1.x | Off |

# 2. TR Table 1 — plant envelope (O.8.2)

| Parameter | TR value | Unit | CCLI yaml | Code |
| --- | --- | --- | --- | --- |
| Max export P (Pfed) | 200 | kW | plant.p_imm_kw | plant_envelope.hpp |
| Max import P (Pass) | 200 | kW | plant.p_ass_kw | plant_envelope.hpp |
| Max inductive Q | 50 | kVAr | plant.q_ind_kvar | plant_envelope.hpp |
| Max capacitive Q | 50 | kVAr | plant.q_cap_kvar | plant_envelope.hpp |
| Smax nameplate | 210 | kVA | plant.smax_kva | smax_kva_effective() |
| IED name | CCI016_01 | — | — | config/icd/cei-tr-57-126-example.cid |
| Eth_A IP (example) | 192.168.8.167 | — | interfaces.eth_a (Phase 2) | lab_tr400.yaml |

# 3. TR Table 1 — active power (Figura 2)

| Parameter | TR value | CCLI yaml / preset |
| --- | --- | --- |
| Wlim | Inactive | dso.wlim_active: false |
| WSd | Active | dso.wsd_active: true (tr57126_table1_dso) |
| WSptPct | +20 % | wspt_pct: 20 |

# 4. Equations & numeric results

(1) Smax_calc = sqrt(max(Pimm²,Pass²)+max(Qind²,Qcap²)) → 206.15 kVA for TR corners.

(1b) Authoritative Smax = 210 kVA (Operating Rule / DPCC3.PdC_VA.VARtg).

(2) P_kW = (pct/100)×Smax → WSd 20% × 210 = 42 kW.

(5)(6) P_effective = min(active caps) → 42 kW (Wlim off, WSd only).

(13)–(17) PF2: apply_dso_to_pf2_config → threshold 42 kW, release 37 kW (release_delta_kw: 5 in lab_tr400_dso_tr57126.yaml).

Gates: dso.enabled AND pf2.use_dso_mock. Measured P: Modbus reg 40001 (kW), not % mock.

# 5. O.7 timing

| Parameter | CEI | Phase 1 CCLI |
| --- | --- | --- |
| TsP active P | ≤ 60 s, ±5 % | settled_within_band_kw() unit only |
| TsQ reactive | ≤ 10 s | Not impl. |
| ΔT slow ring | 10–600 s, default 60 s | Not impl. |
| Set-point spacing | ≥ 3 s (O.7.3.3) | Not impl. |
| TotW period | 4 s (O.8.3) | Modbus poll 1 s |

# 6. Annex T — Wlim (English Table 85 / IT Tab. 84)

| Parameter | Range | Default | Figura 2 TR |
| --- | --- | --- | --- |
| Operating status | 1=Op / 5=Not-Op | 5 | 5 (off) |
| Gen limit | 0..100 % Smax | 0 | inactive |
| Activation | 5=Inactive / 1=Active | 5 | Inactive |

O.9.2.1 trigger: V near 110 % Un — qualitative, no numeric equation.

# 7. Annex T — WSd (English Table 86 / IT Tab. 85)

| Parameter | Range | Default | Figura 2 TR |
| --- | --- | --- | --- |
| Operating status | 1=Op / 5=Not-Op | 5 | 1 (on) |
| WSptPct | ±100 % Smax | 100/0 | +20 % |
| Activation | 5=Inactive / 1=Active | 5 | Active |
| Function status | 0=N/A / 2=Automatic | 2 | Automatic |

# 8. Annex T — reactive (Tables 88–92) — Figura 2 all OFF

| Function | Clause | Key trigger / default | TR Table 1 |
| --- | --- | --- | --- |
| VArSd / s.p. Q | O.9.1.4 | TsQ ≤ 10 s | Inactive |
| PFSP / s.p. cosφ | O.9.1 | cosφ defaults ±0.95 | Inactive |
| VArV / Q(V) | O.9.1.3 | δQ = 5% Qmax | Inactive |
| PFW / cosφ(P) | O.9.1.2 | δcosφ = 0.02 | Inactive |

# 9. CCLI code reference

| Topic | Path |
| --- | --- |
| Regulation map | apps/ccli/core/dso/regulation_map.hpp |
| Plant Eqs (1)(2) | apps/ccli/core/dso/plant_envelope.hpp |
| DSO combine O.11 | apps/ccli/core/dso/dso_active_power.cpp |
| Yaml → PF2 kW | apps/ccli/core/dso/dso_phase1.cpp |
| Config parse | apps/ccli/core/config/ccli_config.cpp |
| Main loop | apps/ccli/services/ccli_main.cpp |
| PF2 FSM | apps/ccli/core/pf2/pf2_fsm.cpp |
| Modbus P | apps/ccli/adapters/modbus_master/modbus_adapter.cpp |
| TR yaml profile | apps/ccli/config/lab_tr400_dso_tr57126.yaml |
| Unit tests | apps/ccli/tests/unit/dso_phase1_test.cpp |
| Master map | lab/PF2_REGULATION_PHASE1.md |

# 10. Phase 1 limitations

WSd → export ceiling for P>threshold FSM; not full O.9.2.3 closed-loop.

Negative WSptPct (import) not mapped.

Wlim/WSd from yaml/preset, not MMS Eth_A.

dso.enabled without pf2.use_dso_mock does not rewrite PF2 kW.

Reactive functions not in core/dso/.

# Appendix — Full Annex T matrix (Figura 2 diagram scope, English extract §5)

Detailed per-function parameters, ranges, defaults, and O.7 timestamps (Tables 85–92). Figura 2 TR instance values in §2–§3 above.

| Function | Timestamp O.7 | Key params | Notes | Figura 2 | Annex T |
| --- | --- | --- | --- | --- | --- |
| lim W110 / lim W (O.9.2.1/2) | TsP ≤ 60 s | Op status 1/5 | Gen limit 0..100% Smax | Default 5 / 0 | Table 85 EN |
| Active power modulation WSd (O.9.2.3) | TsP ≤ 60 s; update ≥ 3 s | Op status 1/5 | Setpoint ±100% Smax | Default 5; TR +20% | Table 86 EN |
| s.p. W WSa (O.10.3.1 MSD) | TsP ≤ 60 s; update ≥ 3 s | Op status 1/5 | Setpoint ±100% Smax | Default 5 | Table 87 EN |
| VArSd (O.9.1.4) | TsQ ≤ 10 s; update ≥ 3 s | Op status 1/5 | Q ±100% Smax | Default 0 | Table 88 EN |
| s.p. Q (O.10.3.2) | TsQ ≤ 10 s | Same as VArSd | — | Inactive TR | Table 89 EN |
| s.p. cosφ PFSP (O.9.1) | TsQ ≤ 10 s | cosφ −1..+1 | Default −0.95 / +0.95 | Inactive TR | Table 90 EN |
| Q(V) VArV (O.9.1.3) | ΔT 10–600 s; TsQ ≤ 10 s | K, lock-in/out, V bands | δQ = 5% Qmax | Inactive TR | Table 91 EN |
| cosφ(P) PFW (O.9.1.2) | ΔT 10–600 s; TsQ ≤ 10 s | Points A/B/C P and cosφ | δcosφ = 0.02 | Inactive TR | Table 92 EN |