# TesPro HW Validation vs CEI 0-16

Central Plant Controller (CCI) — Annex O / T clause traceability
Supplier: TesPro Electronics · Product: TR400 / TG544 / TG-524
Document ID: CCLI-LAB-TESPRO-HW-VAL-001 · Date: 2026-09-22
Normative reference: CEI 0-16 consolidated working edition 2025-12 (Allegato O, T)

Purpose: Request written hardware validation evidence from TesPro for notified body review. Software Phase 1 regulation-check (PF2 equations, DIO logic) is separate from this pack.

# Part 0 — Supplier response (10 priority items)

| # | Clause | Topic | TesPro response |
| --- | --- | --- | --- |
| 1 | O.13.1.1.1 | Eth_A 100BaseFX LC 1310 nm | Module PN? |
| 2 | O.13.1.1.1 | Eth_B 10/100TX or SFP | Which port? |
| 3 | O.13.1 | No bridge between IFs | Firewall proof? |
| 4 | O.13.1.4 | Plant RS485 isolation | ttyS2 vs rs485_2_uart? |
| 5 | O.13.1.4 | No plant on Eth_A/B | Policy doc? |
| 6 | O.13.1.1.2 | Local IF no IP | Product config? |
| 7 | O.13 | EMC / isolation | CE report? |
| 8 | O.13.3 | UPS 1 h | Battery option? |
| 9 | DIO / O.9 | Curtail DO spec | 12 V OK? |
| 10 | T.3.3.4.10 | Traffic segregation | On-box or router? |

# Part A — Annex O O.13 (interfaces & industrial HW)

## A.1 General (O.13)

O.13: Industrial robustness, isolation, EMC, environmental compatibility — request CE/EMC reports.

## A.2 Interface architecture (O.13.1)

| Clause | Requirement | Question to TesPro | Evidence |
| --- | --- | --- | --- |
| O.13.1 | Distinct IFs for DSO, remote actors, plant; plant on separate interfaces. | WAN/LAN1-4/RS485 roles for CCI product? | Network diagram |
| O.13.1 | No data forwarding between CCI comm interfaces; no switch/bridge on CCI data paths. | Default OpenWrt zones; proof Eth_A not routed to plant LAN? | Firewall test procedure |

## A.3 External Ethernet & fibre (O.13.1.1.1)

| Clause | Requirement | Question to TesPro | Evidence |
| --- | --- | --- | --- |
| O.13.1.1.1 | Two IEEE 802.3-2015 external Ethernet IFs: Eth_A (DSO), Eth_B (remote actors). | Which physical ports map to Eth_A vs Eth_B on TR400/TG544/TG-524? | Port map + panel photo |
| O.13.1.1.1 | Eth_A: 100BaseFX, optical, dual LC, 1310 nm multimode fibre. | Onboard FX port or certified SFP/media converter PN? | Module datasheet + compliance |
| O.13.1.1.1 | Eth_B: 10Base-T / 100Base-TX, auto-neg, MDI/MDIX; may be SFP (note 2). | Confirm 10/100 vs GE; SFP option for Eth_B? | PHY/SFP specification |
| O.13.1.1.1 | TCP/IPv4 (mandatory); IPv6 optional; IEC 61850; TLS 1.2+ (62351-3/-8/-9); DHCP; DNS. | Which features enabled on external IFs in product profile? | Config export / app note |
| O.13.1.1.1 | Physical + data-link status in apparatus log; logical service detectable. | How is link status exposed (driver, SNMP, ubus)? | API / log sample |

## A.4 Local commissioning (O.13.1.1.2)

| Clause | Requirement | Question to TesPro | Evidence |
| --- | --- | --- | --- |
| O.13.1.1.2 | Local config: serial or USB only — no IP on commissioning port. | Web/SSH on LAN — how locked for CEI product? | Hardening guide |
| O.13.1.1.2 | User authentication on local access. | Default auth model? | Manual section |

## A.5 DSO / remote logical services (O.13.1.2, O.13.1.3)

| Clause | Requirement | Question to TesPro | Evidence |
| --- | --- | --- | --- |
| O.13.1.2 | Eth_A: IEC 61850 per Annex T; signals only via CCI. | Which port is wired to DSO path? | Install drawing |
| O.13.1.2 | DSO comm loss → autonomous mode (delay per Operating Rule / Annex U). | UPS/battery ≥1 h support (O.13.3)? | Battery/UPS PN |
| O.13.1.3 | Eth_B: remote enabled actors; Annex T cyber. | Which port = Eth_B? | Port map |

## A.6 Plant Modbus / RS485 (O.13.1.4, O.13.1.5)

| Clause | Requirement | Question to TesPro | Evidence |
| --- | --- | --- | --- |
| O.13.1.4 | Plant IF: serial/Ethernet; Modbus RTU/TCP, 61850, etc.; adequate performance. | RS485 isolation rating; max baud; CCLI + seriald sharing? | RS485 chapter + isolation kV |
| O.13.1.4 | Eth_A and Eth_B must NOT be used for plant internal network. | Confirm plant Modbus only on RS485/plant LAN? | Routing policy |
| O.13.1.4 | Monitor CCI ↔ plant comm continuously. | Platform hooks for link monitor? | — |
| Lab | TG544: /dev/ttyS2 (A2/B2 screw) I/O error; LuCI RS485-2 → /dev/rs485_2_uart works. | Production mapping: ttyS2 fix or rs485_2_uart only? | Written confirmation + FW note |

## A.7 Measurement inputs (O.13.2, O.13.2.1)

| Clause | Requirement | Question to TesPro | Evidence |
| --- | --- | --- | --- |
| O.13.2 / O.13.2.1 | PdC V, P, Q inputs; converter accuracy (class ≤0.2 or ≤5% 100–500 kW PV V5). | Use AI1/AI2 or external meter only? | Meter / AI spec |

## A.8 Power & time (O.13.3, O.13.5)

| Clause | Requirement | Question to TesPro | Evidence |
| --- | --- | --- | --- |
| O.13.3 | Backup power ≥1 h for CCI and comm equipment. | Battery option on TG-524? | UPS datasheet |
| O.13.5 | UTC time; uncertainty ≤ ±100 ms. | GNSS vs NTP on platform? | Time sync doc |

## A.9 Data logger — comms events (O.14)

| Clause | Requirement | Question to TesPro | Evidence |
| --- | --- | --- | --- |
| O.14 | Log DSO/external/plant comm; physical & data-link status; cyber events. | Per-port link logging on TesproOS? | logread/syslog example |

# Part B — Digital I/O (PF2 actuation / GD32)

| Clause | Requirement | Question to TesPro | Evidence |
| --- | --- | --- | --- |
| O.9.2.x | Active power limitation at PdC (DSO command mandatory PV/wind ≥100 kW — V5). | DO rating for curtail relay on DIO1? | DIO electrical spec |
| O.13.1 | Plant actuation on separate IF from Eth_A/B. | DIO as plant-side output — confirm. | — |
| O.12 | Installation examples; teledistacco predisposition. | Recommended DIO for Annex M? | Drawing |
| GD32 / DIO1–4 | Field DI/DO via dido_v2 (lab: DIO1 DO curtail, DIO2 DI permissive). | Voltage, current, isolation; DO state on power-down/reboot? | GD32 I/O datasheet |

# Part C — Annex T (cyber / segregation — not fibre PHY)

| Clause | Requirement | Question to TesPro | Evidence |
| --- | --- | --- | --- |
| T.3.3.4.10 | Segregation: NAT, VLAN, firewall, VPN; public net via secure VPN only. | On-box segregation vs external router? | Network architecture PDF |
| T.3.3.4.11 | Secure local commissioning comms. | Same as O.13.1.1.2. | — |
| T.3.2.1 | 61850 measurements every 4 s; performance Type 3. | CPU/ETH load guidance? | — |

# Response log

| Clause | TesPro answer | Evidence file | Status PASS/PART/GAP | Date |
| --- | --- | --- | --- | --- |

# References (HiTEKS repo)

knowledge-base/08-engineering/CCI_Annex_O_Extract.md

knowledge-base/08-engineering/CCI_Annex_T_Extract.md

knowledge-base/08-engineering/CCI_CEI_0-16_Consolidated.md

Architecture/_extracted_reg_analysis/cei_0-16_consolidated_allegato_o_it.txt

lab/TR400_HW_IO_CONFIG.md

lab/PHASE1_LAB_SESSION_FREEZE_2026-09-22.md

Prepared for: TesPro supplier HW validation · HiTEKS CCLI programme