## Reort
|  | System.Windows.Controls.StackPanel | Line Number | Message
Warning
Services
The services section claims support for TimerActivatedControls but "operTm" is not found in model
|  | FALSE | 27 | The services section claims support for TimerActivatedControls but "operTm" is not found in model
1
1
LogControls
Found "ConfLogControl" in Services section but failed to find any Log Control Blocks
|  | FALSE | 38 | Found "ConfLogControl" in Services section but failed to find any Log Control Blocks
1
1
GOOSEControls
Found "GOOSE" in Services section but failed to find any GOOSE Control Blocks
|  | FALSE | 39 | Found "GOOSE" in Services section but failed to find any GOOSE Control Blocks
1
1
DataTypeTemplatesIntegrityCheck
Duplicate Tempate id="APCSelectWithValue_1" found on line number 986" and id="APCOperate_1" found on line number 978
|  | FALSE | 978 | Duplicate Tempate id="APCSelectWithValue_1" found on line number 986" and id="APCOperate_1" found on line number 978
1
Duplicate Tempate id="APCOperate_1" found on line number 978" and id="APCSelectWithValue_1" found on line number 986
|  | FALSE | 986 | Duplicate Tempate id="APCOperate_1" found on line number 978" and id="APCSelectWithValue_1" found on line number 986
1
Duplicate Tempate id="ENCOperate_1" found on line number 1002" and id="ENCSelectWithValue_1" found on line number 994
|  | FALSE | 994 | Duplicate Tempate id="ENCOperate_1" found on line number 1002" and id="ENCSelectWithValue_1" found on line number 994
1
Duplicate Tempate id="ENCSelectWithValue_1" found on line number 994" and id="ENCOperate_1" found on line number 1002
|  | FALSE | 1002 | Duplicate Tempate id="ENCSelectWithValue_1" found on line number 994" and id="ENCOperate_1" found on line number 1002
1
Duplicate Tempate id="Beh" found on line number 1038" and id="Mod" found on line number 1024
|  | FALSE | 1024 | Duplicate Tempate id="Beh" found on line number 1038" and id="Mod" found on line number 1024
1
Duplicate Tempate id="Mod" found on line number 1024" and id="Beh" found on line number 1038
|  | FALSE | 1038 | Duplicate Tempate id="Mod" found on line number 1024" and id="Beh" found on line number 1038
1
Duplicate Tempate id="PhyHealth" found on line number 1050" and id="Health" found on line number 1045
|  | FALSE | 1045 | Duplicate Tempate id="PhyHealth" found on line number 1050" and id="Health" found on line number 1045
1
Duplicate Tempate id="Health" found on line number 1045" and id="PhyHealth" found on line number 1050
|  | FALSE | 1050 | Duplicate Tempate id="Health" found on line number 1045" and id="PhyHealth" found on line number 1050
1
ctlModel="sbo-with-en han ced-secu rity" is not a valid value. Interpreting as "status-only"
|  | FALSE | 423 | ctlModel="sbo-with-en han ced-secu rity" is not a valid value. Interpreting as "status-only"
|  | FALSE | 431 | ctlModel="sbo-with-en han ced-secu rity" is not a valid value. Interpreting as "status-only"
|  | FALSE | 448 | ctlModel="sbo-with-en han ced-secu rity" is not a valid value. Interpreting as "status-only"
|  | FALSE | 461 | ctlModel="sbo-with-en han ced-secu rity" is not a valid value. Interpreting as "status-only"
|  | FALSE | 478 | ctlModel="sbo-with-en han ced-secu rity" is not a valid value. Interpreting as "status-only"
|  | FALSE | 486 | ctlModel="sbo-with-en han ced-secu rity" is not a valid value. Interpreting as "status-only"
|  | FALSE | 503 | ctlModel="sbo-with-en han ced-secu rity" is not a valid value. Interpreting as "status-only"
|  | FALSE | 508 | ctlModel="sbo-with-en han ced-secu rity" is not a valid value. Interpreting as "status-only"
|  | FALSE | 516 | ctlModel="sbo-with-en han ced-secu rity" is not a valid value. Interpreting as "status-only"
|  | FALSE | 536 | ctlModel="sbo-with-en han ced-secu rity" is not a valid value. Interpreting as "status-only"
|  | FALSE | 554 | ctlModel="sbo-with-en han ced-secu rity" is not a valid value. Interpreting as "status-only"
|  | FALSE | 571 | ctlModel="sbo-with-en han ced-secu rity" is not a valid value. Interpreting as "status-only"
|  | FALSE | 619 | ctlModel="sbo-with-en han ced-secu rity" is not a valid value. Interpreting as "status-only"
13
21
Controls
"sboTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "sboTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "sboTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "sboTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "sboTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "sboTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "sboTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "sboTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "sboTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "sboTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "sboTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "sboTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "sboTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "sboTimeout" value is not set in the template or in instance data.
13
"operTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "operTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "operTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "operTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "operTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "operTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "operTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "operTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "operTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "operTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "operTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "operTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "operTimeout" value is not set in the template or in instance data.
|  | FALSE | 0 | "operTimeout" value is not set in the template or in instance data.
13
26
CompareToStandardCustomElement
Failed find "lnClass=DPCC" in master model. Custom LogicalNode?
|  | FALSE | 648 | Failed find "lnClass=DPCC" in master model. Custom LogicalNode?
|  | FALSE | 658 | Failed find "lnClass=DPCC" in master model. Custom LogicalNode?
|  | FALSE | 668 | Failed find "lnClass=DPCC" in master model. Custom LogicalNode?
3
Failed find "lnClass=DECP" in master model. Custom LogicalNode?
|  | FALSE | 678 | Failed find "lnClass=DECP" in master model. Custom LogicalNode?
|  | FALSE | 806 | Failed find "lnClass=DECP" in master model. Custom LogicalNode?
2
Failed find "lnClass=DGEN" in master model. Custom LogicalNode?
|  | FALSE | 685 | Failed find "lnClass=DGEN" in master model. Custom LogicalNode?
|  | FALSE | 729 | Failed find "lnClass=DGEN" in master model. Custom LogicalNode?
2
Failed find "lnClass=DSTO" in master model. Custom LogicalNode?
|  | FALSE | 698 | Failed find "lnClass=DSTO" in master model. Custom LogicalNode?
1
Failed find "lnClass=DWMX" in master model. Custom LogicalNode?
|  | FALSE | 744 | Failed find "lnClass=DWMX" in master model. Custom LogicalNode?
1
Failed find "lnClass=DAGC" in master model. Custom LogicalNode?
|  | FALSE | 754 | Failed find "lnClass=DAGC" in master model. Custom LogicalNode?
1
Failed find "lnClass=DVAR" in master model. Custom LogicalNode?
|  | FALSE | 764 | Failed find "lnClass=DVAR" in master model. Custom LogicalNode?
1
Failed find "lnClass=DFPF" in master model. Custom LogicalNode?
|  | FALSE | 774 | Failed find "lnClass=DFPF" in master model. Custom LogicalNode?
1
Failed find "lnClass=DVVR" in master model. Custom LogicalNode?
|  | FALSE | 786 | Failed find "lnClass=DVVR" in master model. Custom LogicalNode?
1
Failed find "lnClass=DPMC" in master model. Custom LogicalNode?
|  | FALSE | 799 | Failed find "lnClass=DPMC" in master model. Custom LogicalNode?
1
Failed find "lnClass=DPFW" in master model. Custom LogicalNode?
|  | FALSE | 815 | Failed find "lnClass=DPFW" in master model. Custom LogicalNode?
1
15
65
Recommendation
Controls
ctlModel="status-only" parameter "SBOw" is not used
|  | FALSE | 423 | ctlModel="status-only" parameter "SBOw" is not used
|  | FALSE | 431 | ctlModel="status-only" parameter "SBOw" is not used
|  | FALSE | 448 | ctlModel="status-only" parameter "SBOw" is not used
|  | FALSE | 461 | ctlModel="status-only" parameter "SBOw" is not used
|  | FALSE | 478 | ctlModel="status-only" parameter "SBOw" is not used
|  | FALSE | 486 | ctlModel="status-only" parameter "SBOw" is not used
|  | FALSE | 503 | ctlModel="status-only" parameter "SBOw" is not used
|  | FALSE | 508 | ctlModel="status-only" parameter "SBOw" is not used
|  | FALSE | 516 | ctlModel="status-only" parameter "SBOw" is not used
|  | FALSE | 536 | ctlModel="status-only" parameter "SBOw" is not used
|  | FALSE | 554 | ctlModel="status-only" parameter "SBOw" is not used
|  | FALSE | 571 | ctlModel="status-only" parameter "SBOw" is not used
|  | FALSE | 619 | ctlModel="status-only" parameter "SBOw" is not used
13
ctlModel="status-only" parameter "Oper" is not used
|  | FALSE | 423 | ctlModel="status-only" parameter "Oper" is not used
|  | FALSE | 431 | ctlModel="status-only" parameter "Oper" is not used
|  | FALSE | 448 | ctlModel="status-only" parameter "Oper" is not used
|  | FALSE | 461 | ctlModel="status-only" parameter "Oper" is not used
|  | FALSE | 478 | ctlModel="status-only" parameter "Oper" is not used
|  | FALSE | 486 | ctlModel="status-only" parameter "Oper" is not used
|  | FALSE | 503 | ctlModel="status-only" parameter "Oper" is not used
|  | FALSE | 508 | ctlModel="status-only" parameter "Oper" is not used
|  | FALSE | 516 | ctlModel="status-only" parameter "Oper" is not used
|  | FALSE | 536 | ctlModel="status-only" parameter "Oper" is not used
|  | FALSE | 554 | ctlModel="status-only" parameter "Oper" is not used
|  | FALSE | 571 | ctlModel="status-only" parameter "Oper" is not used
|  | FALSE | 619 | ctlModel="status-only" parameter "Oper" is not used
13
ctlModel="status-only" parameter "Cancel" is not used
|  | FALSE | 423 | ctlModel="status-only" parameter "Cancel" is not used
|  | FALSE | 431 | ctlModel="status-only" parameter "Cancel" is not used
|  | FALSE | 448 | ctlModel="status-only" parameter "Cancel" is not used
|  | FALSE | 461 | ctlModel="status-only" parameter "Cancel" is not used
|  | FALSE | 478 | ctlModel="status-only" parameter "Cancel" is not used
|  | FALSE | 486 | ctlModel="status-only" parameter "Cancel" is not used
|  | FALSE | 503 | ctlModel="status-only" parameter "Cancel" is not used
|  | FALSE | 508 | ctlModel="status-only" parameter "Cancel" is not used
|  | FALSE | 516 | ctlModel="status-only" parameter "Cancel" is not used
|  | FALSE | 536 | ctlModel="status-only" parameter "Cancel" is not used
|  | FALSE | 554 | ctlModel="status-only" parameter "Cancel" is not used
|  | FALSE | 571 | ctlModel="status-only" parameter "Cancel" is not used
|  | FALSE | 619 | ctlModel="status-only" parameter "Cancel" is not used
13
39
39
Information
Stats
SCL File is "Edition_2007B4"
|  | FALSE | 0 | SCL File is "Edition_2007B4"
1
There are 0 Private elements and 891 non Private elements.
|  | FALSE | 0 | There are 0 Private elements and 891 non Private elements.
1
There are 0 GGIO Logical Nodes and 31 non GGIO Logical Nodes.
|  | FALSE | 0 | There are 0 GGIO Logical Nodes and 31 non GGIO Logical Nodes.
1
There are 1 Server(s) and 0 Client(s) defined in the file
|  | FALSE | 0 | There are 1 Server(s) and 0 Client(s) defined in the file
1
Report Control Blocks:4 Buffered:1 UnBuffered:3 Instances Supported:8 4 have pre assigned DataSets GOOSE Control Blocks:0 0 have pre assigned DataSets Log Control Blocks:0 0 have pre assigned DataSets Logs:0 SampledValue Control Blocks:0 0 have pre assigned DataSets DataSets:4 Setting Controls:0
|  | FALSE | 0 | Report Control Blocks:4 Buffered:1 UnBuffered:3 Instances Supported:8 4 have pre assigned DataSets GOOSE Control Blocks:0 0 have pre assigned DataSets Log Control Blocks:0 0 have pre assigned DataSets Logs:0 SampledValue Control Blocks:0 0 have pre assigned DataSets DataSets:4 Setting Controls:0
1
5
5
Error
Services
Services section include "SupSubscription" service but no LGOS or LSVS exists in the model
|  | FALSE | 49 | Services section include "SupSubscription" service but no LGOS or LSVS exists in the model
1
1
DataTypeTemplatesIntegrityCheck
Unable to convert value "status-only" of "Mod.ctlModel" to enumeration. See resolved element at line 835
|  | FALSE | 120 | Unable to convert value "status-only" of "Mod.ctlModel" to enumeration. See resolved element at line 835
1
Unable to convert value "status-only" of "Pos.ctlModel" to enumeration. See resolved element at line 920
|  | FALSE | 352 | Unable to convert value "status-only" of "Pos.ctlModel" to enumeration. See resolved element at line 920
1
Unable to convert value "status-only" of "BlkOpn.ctlModel" to enumeration. See resolved element at line 926
|  | FALSE | 357 | Unable to convert value "status-only" of "BlkOpn.ctlModel" to enumeration. See resolved element at line 926
1
Unable to convert value "status-only" of "BlkCls.ctlModel" to enumeration. See resolved element at line 926
|  | FALSE | 362 | Unable to convert value "status-only" of "BlkCls.ctlModel" to enumeration. See resolved element at line 926
1
Unable to convert value "sbo-with-en han ced-secu rity" of "WMaxSptPct.ctlModel" to enumeration. See resolved element at line 932
|  | FALSE | 423 | Unable to convert value "sbo-with-en han ced-secu rity" of "WMaxSptPct.ctlModel" to enumeration. See resolved element at line 932
1
Unable to convert value "sbo-with-en han ced-secu rity" of "Mod.ctlModel" to enumeration. See resolved element at line 941
|  | FALSE | 431 | Unable to convert value "sbo-with-en han ced-secu rity" of "Mod.ctlModel" to enumeration. See resolved element at line 941
|  | FALSE | 461 | Unable to convert value "sbo-with-en han ced-secu rity" of "Mod.ctlModel" to enumeration. See resolved element at line 941
|  | FALSE | 486 | Unable to convert value "sbo-with-en han ced-secu rity" of "Mod.ctlModel" to enumeration. See resolved element at line 941
|  | FALSE | 516 | Unable to convert value "sbo-with-en han ced-secu rity" of "Mod.ctlModel" to enumeration. See resolved element at line 941
|  | FALSE | 536 | Unable to convert value "sbo-with-en han ced-secu rity" of "Mod.ctlModel" to enumeration. See resolved element at line 941
|  | FALSE | 619 | Unable to convert value "sbo-with-en han ced-secu rity" of "Mod.ctlModel" to enumeration. See resolved element at line 941
6
Unable to convert value "sbo-with-en han ced-secu rity" of "WSptPct.ctlModel" to enumeration. See resolved element at line 932
|  | FALSE | 448 | Unable to convert value "sbo-with-en han ced-secu rity" of "WSptPct.ctlModel" to enumeration. See resolved element at line 932
1
Unable to convert value "sbo-with-en han ced-secu rity" of "VArTgtSptPct.ctlModel" to enumeration. See resolved element at line 932
|  | FALSE | 478 | Unable to convert value "sbo-with-en han ced-secu rity" of "VArTgtSptPct.ctlModel" to enumeration. See resolved element at line 932
1
Unable to convert value "sbo-with-en han ced-secu rity" of "PFGnTgtSpt.ctlModel" to enumeration. See resolved element at line 932
|  | FALSE | 503 | Unable to convert value "sbo-with-en han ced-secu rity" of "PFGnTgtSpt.ctlModel" to enumeration. See resolved element at line 932
1
Unable to convert value "sbo-with-en han ced-secu rity" of "PFLodTgtSpt.ctlModel" to enumeration. See resolved element at line 932
|  | FALSE | 508 | Unable to convert value "sbo-with-en han ced-secu rity" of "PFLodTgtSpt.ctlModel" to enumeration. See resolved element at line 932
1
Unable to convert value "sbo-with-en han ced-secu rity" of "WSpt1.ctlModel" to enumeration. See resolved element at line 932
|  | FALSE | 554 | Unable to convert value "sbo-with-en han ced-secu rity" of "WSpt1.ctlModel" to enumeration. See resolved element at line 932
|  | FALSE | 571 | Unable to convert value "sbo-with-en han ced-secu rity" of "WSpt1.ctlModel" to enumeration. See resolved element at line 932
2
17
CompareToStandardPresenceCondition
Missing mandatory element "configRev"
|  | FALSE | 862 | Missing mandatory element "configRev"
1
1
CompareToStandardEnumMismatch
Comparing enum type by ord for element "Mod.stVal". Failed for enumeration "Mod" master value "blocked" != "on-blocked"
|  | FALSE | 1024 | Comparing enum type by ord for element "Mod.stVal". Failed for enumeration "Mod" master value "blocked" != "on-blocked"
1
Comparing enum type by value for element "Mod.stVal". Failed for enumeration "Mod" value="on-blocked" not found in Master Enums.
|  | FALSE | 1024 | Comparing enum type by value for element "Mod.stVal". Failed for enumeration "Mod" value="on-blocked" not found in Master Enums.
1
Comparing enum type by ord for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" master value "status-only" != "statu s-o n ly"
|  | FALSE | 1031 | Comparing enum type by ord for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" master value "status-only" != "statu s-o n ly"
1
Comparing enum type by ord for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" master value "direct-with-normal-security" != "d irect-with-n o rmal-secu rity"
|  | FALSE | 1031 | Comparing enum type by ord for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" master value "direct-with-normal-security" != "d irect-with-n o rmal-secu rity"
1
Comparing enum type by value for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" value="d irect-with-n o rmal-secu rity" not found in Master Enums.
|  | FALSE | 1031 | Comparing enum type by value for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" value="d irect-with-n o rmal-secu rity" not found in Master Enums.
1
Comparing enum type by ord for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" master value "sbo-with-normal-security" != "sbo-with-n o rmal-secu rity"
|  | FALSE | 1031 | Comparing enum type by ord for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" master value "sbo-with-normal-security" != "sbo-with-n o rmal-secu rity"
1
Comparing enum type by value for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" value="sbo-with-n o rmal-secu rity" not found in Master Enums.
|  | FALSE | 1031 | Comparing enum type by value for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" value="sbo-with-n o rmal-secu rity" not found in Master Enums.
1
Comparing enum type by ord for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" master value "direct-with-enhanced-security" != "d irect-with-en h an ced-secu rity"
|  | FALSE | 1031 | Comparing enum type by ord for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" master value "direct-with-enhanced-security" != "d irect-with-en h an ced-secu rity"
1
Comparing enum type by value for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" value="d irect-with-en h an ced-secu rity" not found in Master Enums.
|  | FALSE | 1031 | Comparing enum type by value for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" value="d irect-with-en h an ced-secu rity" not found in Master Enums.
1
Comparing enum type by ord for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" master value "sbo-with-enhanced-security" != "sbo-with-en h an ced-secu rity"
|  | FALSE | 1031 | Comparing enum type by ord for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" master value "sbo-with-enhanced-security" != "sbo-with-en h an ced-secu rity"
1
Comparing enum type by value for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" value="sbo-with-en h an ced-secu rity" not found in Master Enums.
|  | FALSE | 1031 | Comparing enum type by value for element "Mod.ctlModel". Failed for enumeration "CtlModelKind" value="sbo-with-en h an ced-secu rity" not found in Master Enums.
1
Comparing enum type by ord for element "Beh.stVal". Failed for enumeration "Beh" master value "blocked" != "on-blocked"
|  | FALSE | 1038 | Comparing enum type by ord for element "Beh.stVal". Failed for enumeration "Beh" master value "blocked" != "on-blocked"
1
Comparing enum type by value for element "Beh.stVal". Failed for enumeration "Beh" value="on-blocked" not found in Master Enums.
|  | FALSE | 1038 | Comparing enum type by value for element "Beh.stVal". Failed for enumeration "Beh" value="on-blocked" not found in Master Enums.
1
Comparing enum type by ord for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" master value "status-only" != "statu s-o n ly"
|  | FALSE | 1031 | Comparing enum type by ord for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" master value "status-only" != "statu s-o n ly"
1
Comparing enum type by ord for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" master value "direct-with-normal-security" != "d irect-with-n o rmal-secu rity"
|  | FALSE | 1031 | Comparing enum type by ord for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" master value "direct-with-normal-security" != "d irect-with-n o rmal-secu rity"
1
Comparing enum type by value for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" value="d irect-with-n o rmal-secu rity" not found in Master Enums.
|  | FALSE | 1031 | Comparing enum type by value for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" value="d irect-with-n o rmal-secu rity" not found in Master Enums.
1
Comparing enum type by ord for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" master value "sbo-with-normal-security" != "sbo-with-n o rmal-secu rity"
|  | FALSE | 1031 | Comparing enum type by ord for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" master value "sbo-with-normal-security" != "sbo-with-n o rmal-secu rity"
1
Comparing enum type by value for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" value="sbo-with-n o rmal-secu rity" not found in Master Enums.
|  | FALSE | 1031 | Comparing enum type by value for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" value="sbo-with-n o rmal-secu rity" not found in Master Enums.
1
Comparing enum type by ord for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" master value "direct-with-enhanced-security" != "d irect-with-en h an ced-secu rity"
|  | FALSE | 1031 | Comparing enum type by ord for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" master value "direct-with-enhanced-security" != "d irect-with-en h an ced-secu rity"
1
Comparing enum type by value for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" value="d irect-with-en h an ced-secu rity" not found in Master Enums.
|  | FALSE | 1031 | Comparing enum type by value for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" value="d irect-with-en h an ced-secu rity" not found in Master Enums.
1
Comparing enum type by ord for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" master value "sbo-with-enhanced-security" != "sbo-with-en h an ced-secu rity"
|  | FALSE | 1031 | Comparing enum type by ord for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" master value "sbo-with-enhanced-security" != "sbo-with-en h an ced-secu rity"
1
Comparing enum type by value for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" value="sbo-with-en h an ced-secu rity" not found in Master Enums.
|  | FALSE | 1031 | Comparing enum type by value for element "Pos.ctlModel". Failed for enumeration "CtlModelKind" value="sbo-with-en h an ced-secu rity" not found in Master Enums.
1
Comparing enum type by ord for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" master value "status-only" != "statu s-o n ly"
|  | FALSE | 1031 | Comparing enum type by ord for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" master value "status-only" != "statu s-o n ly"
1
Comparing enum type by ord for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" master value "direct-with-normal-security" != "d irect-with-n o rmal-secu rity"
|  | FALSE | 1031 | Comparing enum type by ord for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" master value "direct-with-normal-security" != "d irect-with-n o rmal-secu rity"
1
Comparing enum type by value for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" value="d irect-with-n o rmal-secu rity" not found in Master Enums.
|  | FALSE | 1031 | Comparing enum type by value for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" value="d irect-with-n o rmal-secu rity" not found in Master Enums.
1
Comparing enum type by ord for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" master value "sbo-with-normal-security" != "sbo-with-n o rmal-secu rity"
|  | FALSE | 1031 | Comparing enum type by ord for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" master value "sbo-with-normal-security" != "sbo-with-n o rmal-secu rity"
1
Comparing enum type by value for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" value="sbo-with-n o rmal-secu rity" not found in Master Enums.
|  | FALSE | 1031 | Comparing enum type by value for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" value="sbo-with-n o rmal-secu rity" not found in Master Enums.
1
Comparing enum type by ord for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" master value "direct-with-enhanced-security" != "d irect-with-en h an ced-secu rity"
|  | FALSE | 1031 | Comparing enum type by ord for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" master value "direct-with-enhanced-security" != "d irect-with-en h an ced-secu rity"
1
Comparing enum type by value for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" value="d irect-with-en h an ced-secu rity" not found in Master Enums.
|  | FALSE | 1031 | Comparing enum type by value for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" value="d irect-with-en h an ced-secu rity" not found in Master Enums.
1
Comparing enum type by ord for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" master value "sbo-with-enhanced-security" != "sbo-with-en h an ced-secu rity"
|  | FALSE | 1031 | Comparing enum type by ord for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" master value "sbo-with-enhanced-security" != "sbo-with-en h an ced-secu rity"
1
Comparing enum type by value for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" value="sbo-with-en h an ced-secu rity" not found in Master Enums.
|  | FALSE | 1031 | Comparing enum type by value for element "BlkOpn.ctlModel". Failed for enumeration "CtlModelKind" value="sbo-with-en h an ced-secu rity" not found in Master Enums.
1
Comparing enum type by ord for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" master value "status-only" != "statu s-o n ly"
|  | FALSE | 1031 | Comparing enum type by ord for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" master value "status-only" != "statu s-o n ly"
1
Comparing enum type by ord for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" master value "direct-with-normal-security" != "d irect-with-n o rmal-secu rity"
|  | FALSE | 1031 | Comparing enum type by ord for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" master value "direct-with-normal-security" != "d irect-with-n o rmal-secu rity"
1
Comparing enum type by value for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" value="d irect-with-n o rmal-secu rity" not found in Master Enums.
|  | FALSE | 1031 | Comparing enum type by value for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" value="d irect-with-n o rmal-secu rity" not found in Master Enums.
1
Comparing enum type by ord for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" master value "sbo-with-normal-security" != "sbo-with-n o rmal-secu rity"
|  | FALSE | 1031 | Comparing enum type by ord for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" master value "sbo-with-normal-security" != "sbo-with-n o rmal-secu rity"
1
Comparing enum type by value for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" value="sbo-with-n o rmal-secu rity" not found in Master Enums.
|  | FALSE | 1031 | Comparing enum type by value for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" value="sbo-with-n o rmal-secu rity" not found in Master Enums.
1
Comparing enum type by ord for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" master value "direct-with-enhanced-security" != "d irect-with-en h an ced-secu rity"
|  | FALSE | 1031 | Comparing enum type by ord for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" master value "direct-with-enhanced-security" != "d irect-with-en h an ced-secu rity"
1
Comparing enum type by value for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" value="d irect-with-en h an ced-secu rity" not found in Master Enums.
|  | FALSE | 1031 | Comparing enum type by value for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" value="d irect-with-en h an ced-secu rity" not found in Master Enums.
1
Comparing enum type by ord for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" master value "sbo-with-enhanced-security" != "sbo-with-en h an ced-secu rity"
|  | FALSE | 1031 | Comparing enum type by ord for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" master value "sbo-with-enhanced-security" != "sbo-with-en h an ced-secu rity"
1
Comparing enum type by value for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" value="sbo-with-en h an ced-secu rity" not found in Master Enums.
|  | FALSE | 1031 | Comparing enum type by value for element "BlkCls.ctlModel". Failed for enumeration "CtlModelKind" value="sbo-with-en h an ced-secu rity" not found in Master Enums.
1
40
59