## Mandatory DO audit
LN class | CCI section | DO | CDC | Standard presence (7-4 / 7-420 / 90-9) | Standard source (owner class) | Annex T PresCond (nds/ds) | Result for CCI | In your CID? | Instances missing the DO | Notes
LLN0 | Observability | Beh | ENS | M | IEC 61850-7-4:2010 |  | MANDATORY | YES (all 1 inst.)
LLN0 | Observability | Mod | ENC | M | IEC 61850-7-4:2010 |  | MANDATORY | YES (all 1 inst.) |  | C1: M only in LLN0 of the root LD; optional in all other LNs.
LLN0 | Observability | Health | ENS | M | IEC 61850-7-4:2010 |  | MANDATORY | YES (all 1 inst.) |  | C1: M only in LLN0 of the root LD; optional in all other LNs.
LLN0 | Observability | NamPlt | LPL | M | IEC 61850-7-4:2010 |  | MANDATORY | YES (all 1 inst.) |  | C1: M only in LLN0 of the root LD; optional in all other LNs.
LPHD | Observability | PhyNam | DPL | M | IEC 61850-7-4:2010 | M | MANDATORY | YES (all 1 inst.)
LPHD | Observability | PhyHealth | ENS | M | IEC 61850-7-4:2010 |  | MANDATORY | YES (all 1 inst.)
LPHD | Observability | Proxy | SPS | M | IEC 61850-7-4:2010 |  | MANDATORY | YES (all 1 inst.)
DPCC | Observability | ElcRefId | VSG | M | IEC 61850-7-420 (ElectricalReferenceLN) |  | MANDATORY | YES (all 5 inst.)
DPCC | Observability | VRef | ASG | M | IEC 61850-7-420 (PhysicalElectricalConnectionPointLN) |  | MANDATORY | YES (all 5 inst.)
DPCC | Observability | VArRtg | ASG | O | IEC 61850-7-420 (PhysicalElectricalConnectionPointLN) | R/F | REQUIRED (Annex T, for Annex O function) | PARTIAL | PdC_WiDPCC1, PdC_WaDPCC1, PdC_VADPCC1 | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. Applies only to its own instance: WRtg on PdC_Wi/PdC_Wa, VArRtg on PdC_Qi/PdC_Qc, VARtg on PdC_VA. Other instances correctly lack it.
DPCC | Observability | VARtg | ASG | O | IEC 61850-7-420 (PhysicalElectricalConnectionPointLN) | R/F | REQUIRED (Annex T, for Annex O function) | PARTIAL | PdC_WiDPCC1, PdC_WaDPCC1, PdC_QiDPCC1, PdC_QcDPCC1 | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. Applies only to its own instance: WRtg on PdC_Wi/PdC_Wa, VArRtg on PdC_Qi/PdC_Qc, VARtg on PdC_VA. Other instances correctly lack it.
DPCC | Observability | WRtg | ASG | O | IEC 61850-7-420 (PhysicalElectricalConnectionPointLN) | R/F | REQUIRED (Annex T, for Annex O function) | PARTIAL | PdC_QiDPCC1, PdC_QcDPCC1, PdC_VADPCC1 | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. Applies only to its own instance: WRtg on PdC_Wi/PdC_Wa, VArRtg on PdC_Qi/PdC_Qc, VARtg on PdC_VA. Other instances correctly lack it.
DPCC | Observability | RefFrm | SPG | M | IEC 61850-7-420 (PhysicalElectricalConnectionPointLN) |  | MANDATORY | YES (all 5 inst.)
DPCC | Observability | AreaEpsEcpId | VSG | M | IEC 61850-7-420 (DPCC) |  | MANDATORY | YES (all 5 inst.)
DPCC | Observability | AreaEpsWMax | ASG | M | IEC 61850-7-420 (DPCC) |  | MANDATORY | YES (all 5 inst.)
DPCC | Observability | Beh | ENS | M | IEC 61850-7-4 Common LN |  | MANDATORY | YES (all 5 inst.) |  | Inherited from Common LN / DomainLN: Beh is mandatory in every LN except LPHD.
DECP | Observability + Control (Q(V)) | ElcRefId | VSG | M | IEC 61850-7-420 (ElectricalReferenceLN) |  | MANDATORY | PARTIAL | VArVDECP1, VArVDECP2 | ACTION: add on the VArV DECP instances (mandatory in 7-420).
DECP | Observability + Control (Q(V)) | VRef | ASG | M | IEC 61850-7-420 (PhysicalElectricalConnectionPointLN) |  | MANDATORY | PARTIAL | VArVDECP1, VArVDECP2 | ACTION: add on the VArV DECP instances (mandatory in 7-420).
DECP | Observability + Control (Q(V)) | VMax | ASG | O | IEC 61850-7-420 (PhysicalElectricalConnectionPointLN) | R/F | REQUIRED (Annex T, for Annex O function) | NO | DisFRDECP1, VArVDECP1, VArVDECP2 | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. Annex T requires VMax/VMin on the two Q(V) DECP2 instances (prefix VArV) only.
DECP | Observability + Control (Q(V)) | VMin | ASG | O | IEC 61850-7-420 (PhysicalElectricalConnectionPointLN) | R/F | REQUIRED (Annex T, for Annex O function) | NO | DisFRDECP1, VArVDECP1, VArVDECP2 | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. Annex T requires VMax/VMin on the two Q(V) DECP2 instances (prefix VArV) only.
DECP | Observability + Control (Q(V)) | RefFrm | SPG | M | IEC 61850-7-420 (PhysicalElectricalConnectionPointLN) |  | MANDATORY | PARTIAL | VArVDECP1, VArVDECP2 | ACTION: add on the VArV DECP instances (mandatory in 7-420).
DECP | Observability + Control (Q(V)) | Beh | ENS | M | IEC 61850-7-4 Common LN | M/M | MANDATORY | YES (all 3 inst.) |  | Inherited from Common LN / DomainLN: Beh is mandatory in every LN except LPHD.
DGEN | Observability | OutEcpRef | ORG | M | IEC 61850-7-420 (DER_NameplateRatingsLN) |  | MANDATORY | PARTIAL | SSGGDGEN1, SSGGDGEN2 | ACTION: add to SSGG instances (mandatory in 7-420).
DGEN | Observability | PhsConnTyp | ENG | M | IEC 61850-7-420 (DER_NameplateRatingsLN) |  | MANDATORY | PARTIAL | SSGGDGEN1, SSGGDGEN2 | ACTION: add to SSGG instances (mandatory in 7-420).
DGEN | Observability | DERTyp | ENG | M | IEC 61850-7-420 (DER_NameplateRatingsLN) |  | MANDATORY | PARTIAL | SSGGDGEN1, SSGGDGEN2 | ACTION: add to SSGG instances (mandatory in 7-420).
DGEN | Observability | DEROpSt | ENS | M | IEC 61850-7-420 (DER_StateAbstractLN) |  | MANDATORY | YES (all 3 inst.)
DGEN | Observability | WMax | ASG | M | IEC 61850-7-420 (NonStorageOperationalSettingsLN) |  | MANDATORY | NO | DisFRDGEN1, SSGGDGEN1, SSGGDGEN2 | ACTION: add this DO to the CID model (not to datasets if M/F).
DGEN | Observability | WRmp | ASG | M | IEC 61850-7-420 (NonStorageOperationalSettingsLN) |  | MANDATORY | NO | DisFRDGEN1, SSGGDGEN1, SSGGDGEN2 | ACTION: add this DO to the CID model (not to datasets if M/F).
DGEN | Observability | VMax | ASG | M | IEC 61850-7-420 (NonStorageOperationalSettingsLN) |  | MANDATORY | NO | DisFRDGEN1, SSGGDGEN1, SSGGDGEN2 | ACTION: add this DO to the CID model (not to datasets if M/F).
DGEN | Observability | WMaxRtg | ASG | M | IEC 61850-7-420 (GeneratorNameplateRatingsLN) |  | MANDATORY | NO | DisFRDGEN1, SSGGDGEN1, SSGGDGEN2 | ACTION: add this DO to the CID model (not to datasets if M/F).
DGEN | Observability | VMaxRtg | ASG | M | IEC 61850-7-420 (GeneratorNameplateRatingsLN) |  | MANDATORY | NO | DisFRDGEN1, SSGGDGEN1, SSGGDGEN2 | ACTION: add this DO to the CID model (not to datasets if M/F).
DGEN | Observability | GnOpSt | ENS | M | IEC 61850-7-420 (DGEN) |  | MANDATORY | NO | DisFRDGEN1, SSGGDGEN1, SSGGDGEN2 | ACTION: add this DO to the CID model (not to datasets if M/F).
DGEN | Observability | OpTmsRs | INS | M | IEC 61850-7-420 (DGEN) |  | MANDATORY | NO | DisFRDGEN1, SSGGDGEN1, SSGGDGEN2 | ACTION: add this DO to the CID model (not to datasets if M/F).
DGEN | Observability | Beh | ENS | M | IEC 61850-7-4 Common LN | M/M | MANDATORY | YES (all 3 inst.) |  | Inherited from Common LN / DomainLN: Beh is mandatory in every LN except LPHD.
DGEN | Observability | Health | ENS | C1 (M in LLN0 of root LD; O elsewhere) | IEC 61850-7-4 Common LN | R/O | REQUIRED (Annex T, for Annex O function) | PARTIAL | DisFRDGEN1 | Required by Annex T although O/C in IEC; needed for the Annex O function. Annex T: only on the SSGG instances (single generating units, 1..99).
DGEN | Observability | GnGrId |  | not in IEC std | CEI 0-16 Annex T only (extension) | E/F | REQUIRED (CEI extension) | PARTIAL | DisFRDGEN1 | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. CEI extension: not in IEC 61850; required by Annex T for Annex O functions. Annex T: only on the SSGG instances (single generating units, 1..99).
DSTO | Observability | OutEcpRef | ORG | M | IEC 61850-7-420 (DER_NameplateRatingsLN) |  | MANDATORY | YES (all 1 inst.)
DSTO | Observability | PhsConnTyp | ENG | M | IEC 61850-7-420 (DER_NameplateRatingsLN) |  | MANDATORY | YES (all 1 inst.)
DSTO | Observability | DERTyp | ENG | M | IEC 61850-7-420 (DER_NameplateRatingsLN) |  | MANDATORY | YES (all 1 inst.)
DSTO | Observability | DEROpSt | ENS | M | IEC 61850-7-420 (DER_StateAbstractLN) |  | MANDATORY | YES (all 1 inst.)
DSTO | Observability | EffWh | MV | AtLeastOne (group 1) | IEC 61850-90-9 (StorageOperationalSettingsLN) |  | Optional | YES (all 1 inst.) |  | Choose exactly one (or at least one) DO of the group; Annex T picks the Pct variant where listed.
DSTO | Observability | EffWhPct | MV | AtLeastOne (group 1) | IEC 61850-90-9 (StorageOperationalSettingsLN) |  | Optional | YES (all 1 inst.) |  | Choose exactly one (or at least one) DO of the group; Annex T picks the Pct variant where listed.
DSTO | Observability | ChaWMax | ASG | M | IEC 61850-90-9 (StorageOperationalSettingsLN) |  | MANDATORY | YES (all 1 inst.)
DSTO | Observability | EqSto | ORG | M | IEC 61850-90-9 (DSTO) |  | MANDATORY | YES (all 1 inst.)
DSTO | Observability | Beh | ENS | M | IEC 61850-7-4 Common LN | M/M | MANDATORY | YES (all 1 inst.) |  | Inherited from Common LN / DomainLN: Beh is mandatory in every LN except LPHD.
MMXU | Observability | Beh | ENS | M | IEC 61850-7-4:2010 |  | MANDATORY | PARTIAL | GenPVMMXU1, GenWiMMXU1, GenTerMMXU1, GenIdrMMXU1, StMMXU1, SGGMMXU1, SGGMMXU2 | Inherited from Common LN / DomainLN: Beh is mandatory in every LN except LPHD. ACTION: Beh missing on some MMXU instances (mandatory via Common LN).
MMXU | Observability | TotW | MV | O | IEC 61850-7-4:2010 | R | REQUIRED (Annex T, for Annex O function) | PARTIAL | GenWiMMXU1 | Required by Annex T although O/C in IEC; needed for the Annex O function. Annex T: TotW/TotVAr/PPV on PdC MMXU; only TotW on GenXX, St and SGG MMXU; A is optional.
MMXU | Observability | TotVAr | MV | O | IEC 61850-7-4:2010 | R | REQUIRED (Annex T, for Annex O function) | PARTIAL | GenPVMMXU1, GenWiMMXU1, GenTerMMXU1, GenIdrMMXU1, StMMXU1, SGGMMXU1, SGGMMXU2 | Required by Annex T although O/C in IEC; needed for the Annex O function. Annex T: TotW/TotVAr/PPV on PdC MMXU; only TotW on GenXX, St and SGG MMXU; A is optional.
MMXU | Observability | PPV | DEL | O | IEC 61850-7-4:2010 | R | REQUIRED (Annex T, for Annex O function) | PARTIAL | GenPVMMXU1, GenWiMMXU1, GenTerMMXU1, GenIdrMMXU1, StMMXU1, SGGMMXU1, SGGMMXU2 | Required by Annex T although O/C in IEC; needed for the Annex O function. Annex T: TotW/TotVAr/PPV on PdC MMXU; only TotW on GenXX, St and SGG MMXU; A is optional.
MMXU | Observability | A | WYE | O | IEC 61850-7-4:2010 | O (optional) | Optional | PARTIAL | GenPVMMXU1, GenWiMMXU1, GenTerMMXU1, GenIdrMMXU1, StMMXU1, SGGMMXU1, SGGMMXU2 | Annex T: TotW/TotVAr/PPV on PdC MMXU; only TotW on GenXX, St and SGG MMXU; A is optional.
XCBR | Observability | Beh | ENS | M | IEC 61850-7-4:2010 |  | MANDATORY | YES (all 1 inst.) |  | Inherited from Common LN / DomainLN: Beh is mandatory in every LN except LPHD.
XCBR | Observability | Loc | SPS | M | IEC 61850-7-4:2010 |  | MANDATORY | YES (all 1 inst.)
XCBR | Observability | OpCnt | INS | M | IEC 61850-7-4:2010 |  | MANDATORY | YES (all 1 inst.)
XCBR | Observability | Pos | DPC | M | IEC 61850-7-4:2010 | M | MANDATORY | YES (all 1 inst.)
XCBR | Observability | BlkOpn | SPC | M | IEC 61850-7-4:2010 |  | MANDATORY | YES (all 1 inst.)
XCBR | Observability | BlkCls | SPC | M | IEC 61850-7-4:2010 |  | MANDATORY | YES (all 1 inst.)
DWMX | Control (optional) PF2 | InEcpRef | ORG | M | IEC 61850-7-420 (ElectricalContextReferenceLN) |  | MANDATORY | NO | WlimDWMX1 | ACTION: add this DO to the CID model (not to datasets if M/F).
DWMX | Control (optional) PF2 | RmpRteUse | SPG | M | IEC 61850-7-420 (RampRatesLN) |  | MANDATORY | NO | WlimDWMX1 | ACTION: add this DO to the CID model (not to datasets if M/F).
DWMX | Control (optional) PF2 | WMaxSptPct | APC | AllOnlyOneGroup (group 1) | IEC 61850-7-420 (DWMX) | R/O | REQUIRED (Annex T, for Annex O function) | YES (all 1 inst.) |  | Required by Annex T although O/C in IEC; needed for the Annex O function. Choose exactly one (or at least one) DO of the group; Annex T picks the Pct variant where listed.
DWMX | Control (optional) PF2 | WMaxSpt | APC | AllOnlyOneGroup (group 2) | IEC 61850-7-420 (DWMX) |  | Optional | NO | WlimDWMX1 | Choose exactly one (or at least one) DO of the group; Annex T picks the Pct variant where listed.
DWMX | Control (optional) PF2 | Beh | ENS | M | IEC 61850-7-4 Common LN | M/M | MANDATORY | YES (all 1 inst.) |  | Inherited from Common LN / DomainLN: Beh is mandatory in every LN except LPHD.
DWMX | Control (optional) PF2 | Mod | ENC | C1 (M in LLN0 of root LD; O elsewhere) | IEC 61850-7-4 Common LN | R/O | REQUIRED (Annex T, for Annex O function) | YES (all 1 inst.) |  | Required by Annex T although O/C in IEC; needed for the Annex O function.
DWMX | Control (optional) PF2 | FctOpStAuto |  | not in IEC std | CEI 0-16 Annex T only (extension) | E/F | REQUIRED (CEI extension) | YES (all 1 inst.) |  | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. CEI extension: not in IEC 61850; required by Annex T for Annex O functions.
DWMX | Control (optional) PF2 | FctOpStEx |  | not in IEC std | CEI 0-16 Annex T only (extension) | E/F | REQUIRED (CEI extension) | YES (all 1 inst.) |  | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. CEI extension: not in IEC 61850; required by Annex T for Annex O functions.
DAGC | Control (optional) / MSD | InEcpRef | ORG | M | IEC 61850-7-420 (ElectricalContextReferenceLN) |  | MANDATORY | NO | WSdDAGC1 | ACTION: add this DO to the CID model (not to datasets if M/F).
DAGC | Control (optional) / MSD | RmpRteUse | SPG | M | IEC 61850-7-420 (RampRatesLN) |  | MANDATORY | NO | WSdDAGC1 | ACTION: add this DO to the CID model (not to datasets if M/F).
DAGC | Control (optional) / MSD | ReqW | MV | M | IEC 61850-7-420 (ActivePowerLN) |  | MANDATORY | YES (all 1 inst.)
DAGC | Control (optional) / MSD | WSpt | APC | AllOnlyOneGroup (group 2) | IEC 61850-7-420 (ActivePowerLN) |  | Optional | NO | WSdDAGC1 | Choose exactly one (or at least one) DO of the group; Annex T picks the Pct variant where listed.
DAGC | Control (optional) / MSD | WSptPct | APC | AllOnlyOneGroup (group 1) | IEC 61850-7-420 (ActivePowerLN) | R/O | REQUIRED (Annex T, for Annex O function) | YES (all 1 inst.) |  | Required by Annex T although O/C in IEC; needed for the Annex O function. Choose exactly one (or at least one) DO of the group; Annex T picks the Pct variant where listed.
DAGC | Control (optional) / MSD | Beh | ENS | M | IEC 61850-7-4 Common LN | M/M | MANDATORY | YES (all 1 inst.) |  | Inherited from Common LN / DomainLN: Beh is mandatory in every LN except LPHD.
DAGC | Control (optional) / MSD | Mod | ENC | C1 (M in LLN0 of root LD; O elsewhere) | IEC 61850-7-4 Common LN | R/O | REQUIRED (Annex T, for Annex O function) | YES (all 1 inst.) |  | Required by Annex T although O/C in IEC; needed for the Annex O function.
DAGC | Control (optional) / MSD | FctOpSt |  | not in IEC std | CEI 0-16 Annex T only (extension) | E/F | REQUIRED (CEI extension) | YES (all 1 inst.) |  | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. CEI extension: not in IEC 61850; required by Annex T for Annex O functions.
DVAR | Control (optional) PF2 | InEcpRef | ORG | M | IEC 61850-7-420 (ElectricalContextReferenceLN) |  | MANDATORY | NO | VArSdDVAR1 | ACTION: add this DO to the CID model (not to datasets if M/F).
DVAR | Control (optional) PF2 | RmpRteUse | SPG | M | IEC 61850-7-420 (RampRatesLN) |  | MANDATORY | NO | VArSdDVAR1 | ACTION: add this DO to the CID model (not to datasets if M/F).
DVAR | Control (optional) PF2 | ReqVAr | MV | M | IEC 61850-7-420 (ReactivePowerLN) |  | MANDATORY | YES (all 1 inst.)
DVAR | Control (optional) PF2 | VArTgtSpt | APC | AllOnlyOneGroup (group 1) | IEC 61850-7-420 (ReactivePowerLN) |  | Optional | NO | VArSdDVAR1 | Choose exactly one (or at least one) DO of the group; Annex T picks the Pct variant where listed.
DVAR | Control (optional) PF2 | VArTgtSptPct | APC | AllOnlyOneGroup (group 2) | IEC 61850-7-420 (ReactivePowerLN) | R/O | REQUIRED (Annex T, for Annex O function) | YES (all 1 inst.) |  | Required by Annex T although O/C in IEC; needed for the Annex O function. Choose exactly one (or at least one) DO of the group; Annex T picks the Pct variant where listed.
DVAR | Control (optional) PF2 | Beh | ENS | M | IEC 61850-7-4 Common LN | M/M | MANDATORY | YES (all 1 inst.) |  | Inherited from Common LN / DomainLN: Beh is mandatory in every LN except LPHD.
DVAR | Control (optional) PF2 | Mod | ENC | C1 (M in LLN0 of root LD; O elsewhere) | IEC 61850-7-4 Common LN | R/O | REQUIRED (Annex T, for Annex O function) | YES (all 1 inst.) |  | Required by Annex T although O/C in IEC; needed for the Annex O function.
DVAR | Control (optional) PF2 | FctOpSt |  | not in IEC std | CEI 0-16 Annex T only (extension) | E/F | REQUIRED (CEI extension) | YES (all 1 inst.) |  | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. CEI extension: not in IEC 61850; required by Annex T for Annex O functions.
DFPF | Control (optional) | InEcpRef | ORG | M | IEC 61850-7-420 (ElectricalContextReferenceLN) |  | MANDATORY | NO | PFSPDFPF1 | ACTION: add this DO to the CID model (not to datasets if M/F).
DFPF | Control (optional) | RmpRteUse | SPG | M | IEC 61850-7-420 (RampRatesLN) |  | MANDATORY | NO | PFSPDFPF1 | ACTION: add this DO to the CID model (not to datasets if M/F).
DFPF | Control (optional) | ReqPFExt | SPS | M | IEC 61850-7-420 (DFPF) |  | MANDATORY | YES (all 1 inst.)
DFPF | Control (optional) | ReqPF | MV | M | IEC 61850-7-420 (DFPF) |  | MANDATORY | YES (all 1 inst.)
DFPF | Control (optional) | PFGnTgtSpt | APC | M | IEC 61850-7-420 (DFPF) | M/O | MANDATORY | YES (all 1 inst.)
DFPF | Control (optional) | PFLodTgtSpt | APC | O | IEC 61850-7-420 (DFPF) | R/O | REQUIRED (Annex T, for Annex O function) | YES (all 1 inst.) |  | Required by Annex T although O/C in IEC; needed for the Annex O function.
DFPF | Control (optional) | Beh | ENS | M | IEC 61850-7-4 Common LN | M/M | MANDATORY | YES (all 1 inst.) |  | Inherited from Common LN / DomainLN: Beh is mandatory in every LN except LPHD.
DFPF | Control (optional) | Mod | ENC | C1 (M in LLN0 of root LD; O elsewhere) | IEC 61850-7-4 Common LN | R/O | REQUIRED (Annex T, for Annex O function) | YES (all 1 inst.) |  | Required by Annex T although O/C in IEC; needed for the Annex O function.
DFPF | Control (optional) | FctOpSt |  | not in IEC std | CEI 0-16 Annex T only (extension) | E/F | REQUIRED (CEI extension) | YES (all 1 inst.) |  | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. CEI extension: not in IEC 61850; required by Annex T for Annex O functions.
DVVR | Control (optional) | InEcpRef | ORG | M | IEC 61850-7-420 (ElectricalContextReferenceLN) |  | MANDATORY | NO | VArVDVVR1 | ACTION: add this DO to the CID model (not to datasets if M/F).
DVVR | Control (optional) | RmpRteUse | SPG | M | IEC 61850-7-420 (RampRatesLN) |  | MANDATORY | NO | VArVDVVR1 | ACTION: add this DO to the CID model (not to datasets if M/F).
DVVR | Control (optional) | ReqVAr | MV | M | IEC 61850-7-420 (ReactivePowerLN) |  | MANDATORY | NO | VArVDVVR1 | ACTION: add this DO to the CID model (not to datasets if M/F).
DVVR | Control (optional) | VArTgtSpt | APC | AllOnlyOneGroup (group 1) | IEC 61850-7-420 (ReactivePowerLN) |  | Optional | NO | VArVDVVR1 | Choose exactly one (or at least one) DO of the group; Annex T picks the Pct variant where listed.
DVVR | Control (optional) | VArTgtSptPct | APC | AllOnlyOneGroup (group 2) | IEC 61850-7-420 (ReactivePowerLN) |  | Optional | YES (all 1 inst.) |  | Choose exactly one (or at least one) DO of the group; Annex T picks the Pct variant where listed.
DVVR | Control (optional) | VRefEsp | MV | M | IEC 61850-7-420 (DVVR) |  | MANDATORY | NO | VArVDVVR1 | ACTION: add this DO to the CID model (not to datasets if M/F).
DVVR | Control (optional) | VVArCrv | CSG | AllOnlyOneGroup (group 1) | IEC 61850-7-420 (DVVR) |  | Optional | NO | VArVDVVR1 | Choose exactly one (or at least one) DO of the group; Annex T picks the Pct variant where listed.
DVVR | Control (optional) | VVArCrvDel | CSG | AllOnlyOneGroup (group 2) | IEC 61850-7-420 (DVVR) |  | Optional | YES (all 1 inst.) |  | Choose exactly one (or at least one) DO of the group; Annex T picks the Pct variant where listed.
DVVR | Control (optional) | Beh | ENS | M | IEC 61850-7-4 Common LN | M/M | MANDATORY | YES (all 1 inst.) |  | Inherited from Common LN / DomainLN: Beh is mandatory in every LN except LPHD.
DVVR | Control (optional) | Mod | ENC | C1 (M in LLN0 of root LD; O elsewhere) | IEC 61850-7-4 Common LN | R/O | REQUIRED (Annex T, for Annex O function) | YES (all 1 inst.) |  | Required by Annex T although O/C in IEC; needed for the Annex O function.
DVVR | Control (optional) | FctOpSt |  | not in IEC std | CEI 0-16 Annex T only (extension) | E/F | REQUIRED (CEI extension) | YES (all 1 inst.) |  | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. CEI extension: not in IEC 61850; required by Annex T for Annex O functions.
DVVR | Control (optional) | K |  | not in IEC std | CEI 0-16 Annex T only (extension) | E/F | REQUIRED (CEI extension) | NO | VArVDVVR1 | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. CEI extension: not in IEC 61850; required by Annex T for Annex O functions.
DPMC | Control (optional) | DERRef | ORG | M | IEC 61850-7-420 (DPMC) |  | MANDATORY | NO | VArVDPMC1, VArVDPMC2 | ACTION: add this DO to the CID model (not to datasets if M/F).
DPMC | Control (optional) | OutEcpRef | ORG | M | IEC 61850-7-420 (DPMC) |  | MANDATORY | NO | VArVDPMC1, VArVDPMC2 | ACTION: add this DO to the CID model (not to datasets if M/F).
DPMC | Control (optional) | WSpt1 |  | not in IEC std | CEI 0-16 Annex T only (extension) | R/O | REQUIRED (Annex T, for Annex O function) | YES (all 2 inst.) |  | Required by Annex T although O/C in IEC; needed for the Annex O function.
DPMC | Control (optional) | Beh | ENS | M | IEC 61850-7-4 Common LN |  | MANDATORY | YES (all 2 inst.) |  | Inherited from Common LN / DomainLN: Beh is mandatory in every LN except LPHD.
DPFW | Control (optional, CEI-specific) | Beh | ENS | M | IEC 61850-7-4 Common LN | M/M | MANDATORY | YES (all 1 inst.) |  | LN is CEI-specific (Annex T only); not defined in 7-420 or 90-9. Inherited from Common LN / DomainLN: Beh is mandatory in every LN except LPHD.
DPFW | Control (optional, CEI-specific) | Mod | ENC | C1 (M in LLN0 of root LD; O elsewhere) | IEC 61850-7-4 Common LN | R/O | REQUIRED (Annex T, for Annex O function) | YES (all 1 inst.) |  | LN is CEI-specific (Annex T only); not defined in 7-420 or 90-9. Required by Annex T although O/C in IEC; needed for the Annex O function.
DPFW | Control (optional, CEI-specific) | FctOpSt |  | not in IEC std | CEI 0-16 Annex T only (extension) | M/F | MANDATORY | YES (all 1 inst.) |  | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. LN is CEI-specific (Annex T only); not defined in 7-420 or 90-9.
DPFW | Control (optional, CEI-specific) | WSetA |  | not in IEC std | CEI 0-16 Annex T only (extension) | M/F | MANDATORY | NO | PFWDPFW1 | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. LN is CEI-specific (Annex T only); not defined in 7-420 or 90-9. ACTION: add this DO to the CID model (not to datasets if M/F).
DPFW | Control (optional, CEI-specific) | PFSetA |  | not in IEC std | CEI 0-16 Annex T only (extension) | M/F | MANDATORY | NO | PFWDPFW1 | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. LN is CEI-specific (Annex T only); not defined in 7-420 or 90-9. ACTION: add this DO to the CID model (not to datasets if M/F).
DPFW | Control (optional, CEI-specific) | WSetB |  | not in IEC std | CEI 0-16 Annex T only (extension) | M/F | MANDATORY | NO | PFWDPFW1 | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. LN is CEI-specific (Annex T only); not defined in 7-420 or 90-9. ACTION: add this DO to the CID model (not to datasets if M/F).
DPFW | Control (optional, CEI-specific) | PFSetB |  | not in IEC std | CEI 0-16 Annex T only (extension) | M/F | MANDATORY | NO | PFWDPFW1 | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. LN is CEI-specific (Annex T only); not defined in 7-420 or 90-9. ACTION: add this DO to the CID model (not to datasets if M/F).
DPFW | Control (optional, CEI-specific) | WSetC |  | not in IEC std | CEI 0-16 Annex T only (extension) | M/F | MANDATORY | NO | PFWDPFW1 | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. LN is CEI-specific (Annex T only); not defined in 7-420 or 90-9. ACTION: add this DO to the CID model (not to datasets if M/F).
DPFW | Control (optional, CEI-specific) | PFSetC |  | not in IEC std | CEI 0-16 Annex T only (extension) | M/F | MANDATORY | NO | PFWDPFW1 | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. LN is CEI-specific (Annex T only); not defined in 7-420 or 90-9. ACTION: add this DO to the CID model (not to datasets if M/F).
DPFW | Control (optional, CEI-specific) | VLkIn |  | not in IEC std | CEI 0-16 Annex T only (extension) | M/F | MANDATORY | NO | PFWDPFW1 | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. LN is CEI-specific (Annex T only); not defined in 7-420 or 90-9. ACTION: add this DO to the CID model (not to datasets if M/F).
DPFW | Control (optional, CEI-specific) | VLkOut |  | not in IEC std | CEI 0-16 Annex T only (extension) | M/F | MANDATORY | NO | PFWDPFW1 | F = must not be included in report datasets (Annex T / 7-420 nds/ds). Keep in the model; read on demand. LN is CEI-specific (Annex T only); not defined in 7-420 or 90-9. ACTION: add this DO to the CID model (not to datasets if M/F).

## Legend & sources
Result column | MANDATORY = M in the standard or M in Annex T. REQUIRED = R (O/C in IEC but needed for Annex O) or E (CEI extension). CONDITIONAL = only-one-of / at-least-one group in 7-420/90-9. Optional = listed only because Annex T names it.
Annex T PresCond | nds/ds = non-dataset / dataset. R/F = required in model, forbidden in report datasets. E/F = CEI extension not in datasets. M/M, M/O, R/O as printed.
Sources | CEI 0-16 Annex T (Table 94 legend, T.3.3.1), IEC 61850-7-4:2010 (LLN0 p.24, LPHD p.22, Common LN p.22-23, MMXU p.57-58, XCBR p.105-106), IEC 61850-7-420 NSD 2019A4 and IEC TR 61850-90-9 NSD 2018A3 (machine-readable, inheritance resolved), Annex O for PF1/PF2/PF3.
NIST TN 2217 | US IEEE-1547 profile of 7-420. Its rule "all DOs in the profile are mandatory" applies to the NIST profile only, not to CEI 0-16; not used to set M/O/C.
DPFW | Not defined in 7-420 or 90-9: CEI-specific LN created in Annex T, so its status comes from Annex T only.
Not covered | Common-LN Beh is shown for every LN. Mod/Health/NamPlt are M only in LLN0 of the root LD. 7-4 columns for MMXU list only DOs Annex T selects; all other MMXU DOs are O.
7-420:2021 check | Your 10 class screenshots (7-420:2021 Ed.2, Doc88) use the same nds/ds PresCond column. Checked rows (InEcpRef, RmpRteUse, ReqVAr, VRefEsp, ReqPFExt, OutEcpRef, PhsConnTyp, ElcRefId, RefFrm, WMaxRtg, WRmp) show M/F or M/O, matching the NSD. M/F = must exist in the model, must NOT be put in datasets/reports. The DPCC and DECP PDFs are partial (own DO rows not visible), so those rows rest on the NSD.
CID check basis | "In your CID?" uses your CID LN Values sheet plus the pasted dataset list. A DO defined in the CID without a value or dataset entry may be shown as missing; confirm in the real CID before acting.